## ENVAR Ref
Envar Engineers - Engineering Reference Sheet
Ver 1.1
DUCT DESIGN | [7 empty] | Errors | 0 | 35 | 80 | 150 | 210 | 280 | 380 |  |  | 150 | 200 | 250 | 300 | 350 | 400 | 450
| L/s | Diameter |  | Max Height | Spigot Length |  |  |  | 36 | 81 | 151 | 211 | 281 | 381 | 476 |  | 100H | 178L | 256L
flexible duct |  | - | oval spigots |  | - |  |  |  | 150 | 200 | 250 | 300 | 350 | 400 | 450 |  | 150H |  | 228L | 306L | 384L
*Envar |  |  | *Bullocks | [13 empty] | 200H |  |  | 278L | 356L | 434L
| L/s | Temp. ΔT | Capacity kW | Current Amps | [12 empty] | 250H |  |  |  |  | 406L | 484L | 562L
electric duct heater |  |  | - | - | [5 empty] | 10 | 15 | [5 empty] | 300H | [5 empty] | 456L | 534L
*Grimwood
DIFFUSION
| L/s | plenum length | # of Slots | [5 empty] | -
linear slots |  |  | -
*SW Hart
| L/s | Velocity m/s | Neck Size mm | Grille Sq.m |  |  |  |  | grille velocity m/s
4-way blow |  |  | - | - |  |  |  |  | 1 | 1.1 | 1.2 | 1.3 | 1.4 | 1.5 | 1.6 | 1.7 | 1.8 | 1.9 | 2 | 2.1 | 2.2 | 2.3 | 2.4 | 2.5 | 2.6 | 2.7 | 2.8 | 2.9 | 3 | 3.1 | 3.2 | 3.3 | 3.4 | 3.5 | 3.6 | 3.7 | 3.8 | 3.9 | 4 | 4.1 | 4.2 | 4.3 | 4.4 | 4.5 | 4.6 | 4.7 | 4.8 | 4.9 | 5 | 5.1 | 5.2 | 5.3 | 5.4 | 5.5 | 5.6 | 5.7 | 5.8 | 5.9 | 6
*SW Hart
| L/s | Velocity m/s | Known Width | x Height | Sq. Grille Size | Grille Sq.m
louvre/door grille |  |  |  | - | - | -
*SW Hart
| L/s | Velocity m/s | Known Width | x Height | Sq. Grille Size | Grille Sq.m
eggcrate grille |  |  |  | - | - | -
*SW Hart
| L/s | Velocity m/s | Known Width | x Height | Sq. Grille Size | Grille Sq.m
bar grille/half chevron | 125 | 2 |  | - | 300 | 0.09375
*SW Hart
| L/s | Neck Size | Collar Size | [5 empty] | grille velocity m/s 1: grille face sizes
swirl diffuser |  | - | - | [5 empty] | grille velocity m/s 1: 355mm; grille velocity m/s 1.1: 500mm
*Krantz
| L/s | F/A Mesh | Velocity m/s | Known Width | x Height | Sq. Grille Size | Grille Sq.m |  | grille velocity m/s 1: perf free/area
perforated grille |  |  |  |  | - | - | - |  | grille velocity m/s 1.1: 51%; grille velocity m/s 1.2: 62%
*SW Hart
PIPE SYSTEMS

## Ductulator
Ductulator
|  | Airflow Rate |  | 240 | l/s |  |  | Duct Length | [10 empty] | Legend [m/s]
|  | Velocity |  | 240 | m/s |  |  | Duct Width |  | 250
|  | Flowrate |  | 864 | m3/h |  |  | Pa/m Loss |  | #VALUE! | *Select Cell & Press F9 | [6 empty] | < 2,0
2,0 - 3,0
Speed Through Round Duct | [17 empty] | 3,0 - 4,0
80 | 90 | 100 | 112 | 125 | 150 | 160 | 180 | 200 | 225 | 250 | 280 | 315 | 400 | 500 |  |  |  | 4,0 - 5,0
47.7465 | 37.7256 | 30.5577 | 24.3605 | 19.557 | 13.5812 | 11.9366 | 9.4314 | 7.6394 | 6.0361 | 4.8892 | 3.8977 | 3.0796 | 1.9099 | 1.2223 |  |  |  | > 5,0
Speed Through Square Duct W x h
l x w | 100 | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 500 | 550 | 600 | 650 | 700 | 750 | 800 | 850 | 900 | 950 | 1000 | 1050 | 1100 | 1150 | 1200 | 1250 | 1300 | 1350 | 1400 | 1450 | 1500 | 1550 | 1600 | 1650 | 1700 | 1750 | 1800 | 1850 | 1900 | 1950 | 2000
100 | 24
150 | 16 | 10.6667
200 | 12 | 8 | 6
250 | 9.6 | 6.4 | 4.8 | 3.84
300 | 8 | 5.3333 | 4 | 3.2 | 2.6667
350 | 6.8571 | 4.5714 | 3.4286 | 2.7429 | 2.2857 | 1.9592
400 | 6 | 4 | 3 | 2.4 | 2 | 1.7143 | 1.5
450 | 5.3333 | 3.5556 | 2.6667 | 2.1333 | 1.7778 | 1.5238 | 1.3333 | 1.1852
500 | 4.8 | 3.2 | 2.4 | 1.92 | 1.6 | 1.3714 | 1.2 | 1.0667 | 0.96
550 | 4.3636 | 2.9091 | 2.1818 | 1.7455 | 1.4545 | 1.2468 | 1.0909 | 0.9697 | 0.87273 | 0.79339
600 | 4 | 2.6667 | 2 | 1.6 | 1.3333 | 1.1429 | 1 | 0.88889 | 0.8 | 0.72727 | 0.66667
650 | 3.6923 | 2.4615 | 1.8462 | 1.4769 | 1.2308 | 1.0549 | 0.92308 | 0.82051 | 0.73846 | 0.67133 | 0.61538 | 0.56805
700 | 3.4286 | 2.2857 | 1.7143 | 1.3714 | 1.1429 | 0.97959 | 0.85714 | 0.7619 | 0.68571 | 0.62338 | 0.57143 | 0.52747 | 0.4898
750 | 3.2 | 2.1333 | 1.6 | 1.28 | 1.0667 | 0.91429 | 0.8 | 0.71111 | 0.64 | 0.58182 | 0.53333 | 0.49231 | 0.45714 | 0.42667
800 | 3 | 2 | 1.5 | 1.2 | 1 | 0.85714 | 0.75 | 0.66667 | 0.6 | 0.54545 | 0.5 | 0.46154 | 0.42857 | 0.4 | 0.375
850 | 2.8235 | 1.8824 | 1.4118 | 1.1294 | 0.94118 | 0.80672 | 0.70588 | 0.62745 | 0.56471 | 0.51337 | 0.47059 | 0.43439 | 0.40336 | 0.37647 | 0.35294 | 0.33218
900 | 2.6667 | 1.7778 | 1.3333 | 1.0667 | 0.88889 | 0.7619 | 0.66667 | 0.59259 | 0.53333 | 0.48485 | 0.44444 | 0.41026 | 0.38095 | 0.35556 | 0.33333 | 0.31373 | 0.2963
950 | 2.5263 | 1.6842 | 1.2632 | 1.0105 | 0.84211 | 0.7218 | 0.63158 | 0.5614 | 0.50526 | 0.45933 | 0.42105 | 0.38866 | 0.3609 | 0.33684 | 0.31579 | 0.29721 | 0.2807 | 0.26593
1000 | 2.4 | 1.6 | 1.2 | 0.96 | 0.8 | 0.68571 | 0.6 | 0.53333 | 0.48 | 0.43636 | 0.4 | 0.36923 | 0.34286 | 0.32 | 0.3 | 0.28235 | 0.26667 | 0.25263 | 0.24
1050 | 2.2857 | 1.5238 | 1.1429 | 0.91429 | 0.7619 | 0.65306 | 0.57143 | 0.50794 | 0.45714 | 0.41558 | 0.38095 | 0.35165 | 0.32653 | 0.30476 | 0.28571 | 0.26891 | 0.25397 | 0.2406 | 0.22857 | 0.21769
1100 | 2.1818 | 1.4545 | 1.0909 | 0.87273 | 0.72727 | 0.62338 | 0.54545 | 0.48485 | 0.43636 | 0.39669 | 0.36364 | 0.33566 | 0.31169 | 0.29091 | 0.27273 | 0.25668 | 0.24242 | 0.22967 | 0.21818 | 0.20779 | 0.19835
1150 | 2.087 | 1.3913 | 1.0435 | 0.83478 | 0.69565 | 0.59627 | 0.52174 | 0.46377 | 0.41739 | 0.37945 | 0.34783 | 0.32107 | 0.29814 | 0.27826 | 0.26087 | 0.24552 | 0.23188 | 0.21968 | 0.2087 | 0.19876 | 0.18972 | 0.18147
1200 | 2 | 1.3333 | 1 | 0.8 | 0.66667 | 0.57143 | 0.5 | 0.44444 | 0.4 | 0.36364 | 0.33333 | 0.30769 | 0.28571 | 0.26667 | 0.25 | 0.23529 | 0.22222 | 0.21053 | 0.2 | 0.19048 | 0.18182 | 0.17391 | 0.16667
1250 | 1.92 | 1.28 | 0.96 | 0.768 | 0.64 | 0.54857 | 0.48 | 0.42667 | 0.384 | 0.34909 | 0.32 | 0.29538 | 0.27429 | 0.256 | 0.24 | 0.22588 | 0.21333 | 0.20211 | 0.192 | 0.18286 | 0.17455 | 0.16696 | 0.16 | 0.1536
1300 | 1.8462 | 1.2308 | 0.92308 | 0.73846 | 0.61538 | 0.52747 | 0.46154 | 0.41026 | 0.36923 | 0.33566 | 0.30769 | 0.28402 | 0.26374 | 0.24615 | 0.23077 | 0.21719 | 0.20513 | 0.19433 | 0.18462 | 0.17582 | 0.16783 | 0.16054 | 0.15385 | 0.14769 | 0.14201
1350 | 1.7778 | 1.1852 | 0.88889 | 0.71111 | 0.59259 | 0.50794 | 0.44444 | 0.39506 | 0.35556 | 0.32323 | 0.2963 | 0.2735 | 0.25397 | 0.23704 | 0.22222 | 0.20915 | 0.19753 | 0.18713 | 0.17778 | 0.16931 | 0.16162 | 0.15459 | 0.14815 | 0.14222 | 0.13675 | 0.13169
1400 | 1.7143 | 1.1429 | 0.85714 | 0.68571 | 0.57143 | 0.4898 | 0.42857 | 0.38095 | 0.34286 | 0.31169 | 0.28571 | 0.26374 | 0.2449 | 0.22857 | 0.21429 | 0.20168 | 0.19048 | 0.18045 | 0.17143 | 0.16327 | 0.15584 | 0.14907 | 0.14286 | 0.13714 | 0.13187 | 0.12698 | 0.12245 | 0.11823 | 0.11429 | 0.1106 | 0.10714 | 0.1039 | 0.10084 | 0.097959 | 0.095238 | 0.092664 | 0.090226 | 0.087912 | 0.085714
1450 | 1.6552 | 1.1034 | 0.82759 | 0.66207 | 0.55172 | 0.47291 | 0.41379 | 0.36782 | 0.33103 | 0.30094 | 0.27586 | 0.25464 | 0.23645 | 0.22069 | 0.2069 | 0.19473 | 0.18391 | 0.17423 | 0.16552 | 0.15764 | 0.15047 | 0.14393 | 0.13793 | 0.13241 | 0.12732 | 0.12261 | 0.11823 | 0.11415 | 0.11034 | 0.10679 | 0.10345 | 0.10031 | 0.097363 | 0.094581 | 0.091954 | 0.089469 | 0.087114 | 0.084881 | 0.082759
1500 | 1.6 | 1.0667 | 0.8 | 0.64 | 0.53333 | 0.45714 | 0.4 | 0.35556 | 0.32 | 0.29091 | 0.26667 | 0.24615 | 0.22857 | 0.21333 | 0.2 | 0.18824 | 0.17778 | 0.16842 | 0.16 | 0.15238 | 0.14545 | 0.13913 | 0.13333 | 0.128 | 0.12308 | 0.11852 | 0.11429 | 0.11034 | 0.10667 | 0.10323 | 0.1 | 0.09697 | 0.094118 | 0.091429 | 0.088889 | 0.086486 | 0.084211 | 0.082051 | 0.08
1550 | 1.5484 | 1.0323 | 0.77419 | 0.61935 | 0.51613 | 0.4424 | 0.3871 | 0.34409 | 0.30968 | 0.28152 | 0.25806 | 0.23821 | 0.2212 | 0.20645 | 0.19355 | 0.18216 | 0.17204 | 0.16299 | 0.15484 | 0.14747 | 0.14076 | 0.13464 | 0.12903 | 0.12387 | 0.11911 | 0.1147 | 0.1106 | 0.10679 | 0.10323 | 0.099896 | 0.096774 | 0.093842 | 0.091082 | 0.088479 | 0.086022 | 0.083697 | 0.081494 | 0.079404 | 0.077419
1600 | 1.5 | 1 | 0.75 | 0.6 | 0.5 | 0.42857 | 0.375 | 0.33333 | 0.3 | 0.27273 | 0.25 | 0.23077 | 0.21429 | 0.2 | 0.1875 | 0.17647 | 0.16667 | 0.15789 | 0.15 | 0.14286 | 0.13636 | 0.13043 | 0.125 | 0.12 | 0.11538 | 0.11111 | 0.10714 | 0.10345 | 0.1 | 0.096774 | 0.09375 | 0.090909 | 0.088235 | 0.085714 | 0.083333 | 0.081081 | 0.078947 | 0.076923 | 0.075
1650 | 1.4545 | 0.9697 | 0.72727 | 0.58182 | 0.48485 | 0.41558 | 0.36364 | 0.32323 | 0.29091 | 0.26446 | 0.24242 | 0.22378 | 0.20779 | 0.19394 | 0.18182 | 0.17112 | 0.16162 | 0.15311 | 0.14545 | 0.13853 | 0.13223 | 0.12648 | 0.12121 | 0.11636 | 0.11189 | 0.10774 | 0.1039 | 0.10031 | 0.09697 | 0.093842 | 0.090909 | 0.088154 | 0.085561 | 0.083117 | 0.080808 | 0.078624 | 0.076555 | 0.074592 | 0.072727
1700 | 1.4118 | 0.94118 | 0.70588 | 0.56471 | 0.47059 | 0.40336 | 0.35294 | 0.31373 | 0.28235 | 0.25668 | 0.23529 | 0.21719 | 0.20168 | 0.18824 | 0.17647 | 0.16609 | 0.15686 | 0.14861 | 0.14118 | 0.13445 | 0.12834 | 0.12276 | 0.11765 | 0.11294 | 0.1086 | 0.10458 | 0.10084 | 0.097363 | 0.094118 | 0.091082 | 0.088235 | 0.085561 | 0.083045 | 0.080672 | 0.078431 | 0.076312 | 0.074303 | 0.072398 | 0.070588
1750 | 1.3714 | 0.91429 | 0.68571 | 0.54857 | 0.45714 | 0.39184 | 0.34286 | 0.30476 | 0.27429 | 0.24935 | 0.22857 | 0.21099 | 0.19592 | 0.18286 | 0.17143 | 0.16134 | 0.15238 | 0.14436 | 0.13714 | 0.13061 | 0.12468 | 0.11925 | 0.11429 | 0.10971 | 0.10549 | 0.10159 | 0.097959 | 0.094581 | 0.091429 | 0.088479 | 0.085714 | 0.083117 | 0.080672 | 0.078367 | 0.07619 | 0.074131 | 0.07218 | 0.07033 | 0.068571
1800 | 1.3333 | 0.88889 | 0.66667 | 0.53333 | 0.44444 | 0.38095 | 0.33333 | 0.2963 | 0.26667 | 0.24242 | 0.22222 | 0.20513 | 0.19048 | 0.17778 | 0.16667 | 0.15686 | 0.14815 | 0.14035 | 0.13333 | 0.12698 | 0.12121 | 0.11594 | 0.11111 | 0.10667 | 0.10256 | 0.098765 | 0.095238 | 0.091954 | 0.088889 | 0.086022 | 0.083333 | 0.080808 | 0.078431 | 0.07619 | 0.074074 | 0.072072 | 0.070175 | 0.068376 | 0.066667
1850 | 1.2973 | 0.86486 | 0.64865 | 0.51892 | 0.43243 | 0.37066 | 0.32432 | 0.28829 | 0.25946 | 0.23587 | 0.21622 | 0.19958 | 0.18533 | 0.17297 | 0.16216 | 0.15262 | 0.14414 | 0.13656 | 0.12973 | 0.12355 | 0.11794 | 0.11281 | 0.10811 | 0.10378 | 0.099792 | 0.096096 | 0.092664 | 0.089469 | 0.086486 | 0.083697 | 0.081081 | 0.078624 | 0.076312 | 0.074131 | 0.072072 | 0.070124 | 0.068279 | 0.066528 | 0.064865
1900 | 1.2632 | 0.84211 | 0.63158 | 0.50526 | 0.42105 | 0.3609 | 0.31579 | 0.2807 | 0.25263 | 0.22967 | 0.21053 | 0.19433 | 0.18045 | 0.16842 | 0.15789 | 0.14861 | 0.14035 | 0.13296 | 0.12632 | 0.1203 | 0.11483 | 0.10984 | 0.10526 | 0.10105 | 0.097166 | 0.093567 | 0.090226 | 0.087114 | 0.084211 | 0.081494 | 0.078947 | 0.076555 | 0.074303 | 0.07218 | 0.070175 | 0.068279 | 0.066482 | 0.064777 | 0.063158
1950 | 1.2308 | 0.82051 | 0.61538 | 0.49231 | 0.41026 | 0.35165 | 0.30769 | 0.2735 | 0.24615 | 0.22378 | 0.20513 | 0.18935 | 0.17582 | 0.1641 | 0.15385 | 0.1448 | 0.13675 | 0.12955 | 0.12308 | 0.11722 | 0.11189 | 0.10702 | 0.10256 | 0.098462 | 0.094675 | 0.091168 | 0.087912 | 0.084881 | 0.082051 | 0.079404 | 0.076923 | 0.074592 | 0.072398 | 0.07033 | 0.068376 | 0.066528 | 0.064777 | 0.063116 | 0.061538
2000 | 1.2 | 0.8 | 0.6 | 0.48 | 0.4 | 0.34286 | 0.3 | 0.26667 | 0.24 | 0.21818 | 0.2 | 0.18462 | 0.17143 | 0.16 | 0.15 | 0.14118 | 0.13333 | 0.12632 | 0.12 | 0.11429 | 0.10909 | 0.10435 | 0.1 | 0.096 | 0.092308 | 0.088889 | 0.085714 | 0.082759 | 0.08 | 0.077419 | 0.075 | 0.072727 | 0.070588 | 0.068571 | 0.066667 | 0.064865 | 0.063158 | 0.061538 | 0.06
2050 | 1.1707 | 0.78049 | 0.58537 | 0.46829 | 0.39024 | 0.33449 | 0.29268 | 0.26016 | 0.23415 | 0.21286 | 0.19512 | 0.18011 | 0.16725 | 0.1561 | 0.14634 | 0.13773 | 0.13008 | 0.12323 | 0.11707 | 0.1115 | 0.10643 | 0.1018 | 0.097561 | 0.093659 | 0.090056 | 0.086721 | 0.083624 | 0.08074 | 0.078049 | 0.075531 | 0.073171 | 0.070953 | 0.068867 | 0.066899 | 0.065041 | 0.063283 | 0.061617 | 0.060038 | 0.058537
2100 | 1.1429 | 0.7619 | 0.57143 | 0.45714 | 0.38095 | 0.32653 | 0.28571 | 0.25397 | 0.22857 | 0.20779 | 0.19048 | 0.17582 | 0.16327 | 0.15238 | 0.14286 | 0.13445 | 0.12698 | 0.1203 | 0.11429 | 0.10884 | 0.1039 | 0.099379 | 0.095238 | 0.091429 | 0.087912 | 0.084656 | 0.081633 | 0.078818 | 0.07619 | 0.073733 | 0.071429 | 0.069264 | 0.067227 | 0.065306 | 0.063492 | 0.061776 | 0.06015 | 0.058608 | 0.057143
2150 | 1.1163 | 0.74419 | 0.55814 | 0.44651 | 0.37209 | 0.31894 | 0.27907 | 0.24806 | 0.22326 | 0.20296 | 0.18605 | 0.17174 | 0.15947 | 0.14884 | 0.13953 | 0.13133 | 0.12403 | 0.1175 | 0.11163 | 0.10631 | 0.10148 | 0.097068 | 0.093023 | 0.089302 | 0.085868 | 0.082687 | 0.079734 | 0.076985 | 0.074419 | 0.072018 | 0.069767 | 0.067653 | 0.065663 | 0.063787 | 0.062016 | 0.060339 | 0.058752 | 0.057245 | 0.055814
2200 | 1.0909 | 0.72727 | 0.54545 | 0.43636 | 0.36364 | 0.31169 | 0.27273 | 0.24242 | 0.21818 | 0.19835 | 0.18182 | 0.16783 | 0.15584 | 0.14545 | 0.13636 | 0.12834 | 0.12121 | 0.11483 | 0.10909 | 0.1039 | 0.099174 | 0.094862 | 0.090909 | 0.087273 | 0.083916 | 0.080808 | 0.077922 | 0.075235 | 0.072727 | 0.070381 | 0.068182 | 0.066116 | 0.064171 | 0.062338 | 0.060606 | 0.058968 | 0.057416 | 0.055944 | 0.054545
2250 | 1.0667 | 0.71111 | 0.53333 | 0.42667 | 0.35556 | 0.30476 | 0.26667 | 0.23704 | 0.21333 | 0.19394 | 0.17778 | 0.1641 | 0.15238 | 0.14222 | 0.13333 | 0.12549 | 0.11852 | 0.11228 | 0.10667 | 0.10159 | 0.09697 | 0.092754 | 0.088889 | 0.085333 | 0.082051 | 0.079012 | 0.07619 | 0.073563 | 0.071111 | 0.068817 | 0.066667 | 0.064646 | 0.062745 | 0.060952 | 0.059259 | 0.057658 | 0.05614 | 0.054701 | 0.053333
2300 | 1.0435 | 0.69565 | 0.52174 | 0.41739 | 0.34783 | 0.29814 | 0.26087 | 0.23188 | 0.2087 | 0.18972 | 0.17391 | 0.16054 | 0.14907 | 0.13913 | 0.13043 | 0.12276 | 0.11594 | 0.10984 | 0.10435 | 0.099379 | 0.094862 | 0.090737 | 0.086957 | 0.083478 | 0.080268 | 0.077295 | 0.074534 | 0.071964 | 0.069565 | 0.067321 | 0.065217 | 0.063241 | 0.061381 | 0.059627 | 0.057971 | 0.056404 | 0.05492 | 0.053512 | 0.052174
2350 | 1.0213 | 0.68085 | 0.51064 | 0.40851 | 0.34043 | 0.29179 | 0.25532 | 0.22695 | 0.20426 | 0.18569 | 0.17021 | 0.15712 | 0.1459 | 0.13617 | 0.12766 | 0.12015 | 0.11348 | 0.1075 | 0.10213 | 0.097264 | 0.092843 | 0.088807 | 0.085106 | 0.081702 | 0.07856 | 0.07565 | 0.072948 | 0.070433 | 0.068085 | 0.065889 | 0.06383 | 0.061896 | 0.060075 | 0.058359 | 0.056738 | 0.055204 | 0.053751 | 0.052373 | 0.051064
2400 | 1 | 0.66667 | 0.5 | 0.4 | 0.33333 | 0.28571 | 0.25 | 0.22222 | 0.2 | 0.18182 | 0.16667 | 0.15385 | 0.14286 | 0.13333 | 0.125 | 0.11765 | 0.11111 | 0.10526 | 0.1 | 0.095238 | 0.090909 | 0.086957 | 0.083333 | 0.08 | 0.076923 | 0.074074 | 0.071429 | 0.068966 | 0.066667 | 0.064516 | 0.0625 | 0.060606 | 0.058824 | 0.057143 | 0.055556 | 0.054054 | 0.052632 | 0.051282 | 0.05
2450 | 0.97959 | 0.65306 | 0.4898 | 0.39184 | 0.32653 | 0.27988 | 0.2449 | 0.21769 | 0.19592 | 0.17811 | 0.16327 | 0.15071 | 0.13994 | 0.13061 | 0.12245 | 0.11525 | 0.10884 | 0.10311 | 0.097959 | 0.093294 | 0.089054 | 0.085182 | 0.081633 | 0.078367 | 0.075353 | 0.072562 | 0.069971 | 0.067558 | 0.065306 | 0.063199 | 0.061224 | 0.059369 | 0.057623 | 0.055977 | 0.054422 | 0.052951 | 0.051557 | 0.050235 | 0.04898
2500 | 0.96 | 0.64 | 0.48 | 0.384 | 0.32 | 0.27429 | 0.24 | 0.21333 | 0.192 | 0.17455 | 0.16 | 0.14769 | 0.13714 | 0.128 | 0.12 | 0.11294 | 0.10667 | 0.10105 | 0.096 | 0.091429 | 0.087273 | 0.083478 | 0.08 | 0.0768 | 0.073846 | 0.071111 | 0.068571 | 0.066207 | 0.064 | 0.061935 | 0.06 | 0.058182 | 0.056471 | 0.054857 | 0.053333 | 0.051892 | 0.050526 | 0.049231 | 0.048
2550 | 0.94118 | 0.62745 | 0.47059 | 0.37647 | 0.31373 | 0.26891 | 0.23529 | 0.20915 | 0.18824 | 0.17112 | 0.15686 | 0.1448 | 0.13445 | 0.12549 | 0.11765 | 0.11073 | 0.10458 | 0.099071 | 0.094118 | 0.089636 | 0.085561 | 0.081841 | 0.078431 | 0.075294 | 0.072398 | 0.069717 | 0.067227 | 0.064909 | 0.062745 | 0.060721 | 0.058824 | 0.057041 | 0.055363 | 0.053782 | 0.052288 | 0.050874 | 0.049536 | 0.048265 | 0.047059
2600 | 0.92308 | 0.61538 | 0.46154 | 0.36923 | 0.30769 | 0.26374 | 0.23077 | 0.20513 | 0.18462 | 0.16783 | 0.15385 | 0.14201 | 0.13187 | 0.12308 | 0.11538 | 0.1086 | 0.10256 | 0.097166 | 0.092308 | 0.087912 | 0.083916 | 0.080268 | 0.076923 | 0.073846 | 0.071006 | 0.068376 | 0.065934 | 0.06366 | 0.061538 | 0.059553 | 0.057692 | 0.055944 | 0.054299 | 0.052747 | 0.051282 | 0.049896 | 0.048583 | 0.047337 | 0.046154
2650 | 0.90566 | 0.60377 | 0.45283 | 0.36226 | 0.30189 | 0.25876 | 0.22642 | 0.20126 | 0.18113 | 0.16467 | 0.15094 | 0.13933 | 0.12938 | 0.12075 | 0.11321 | 0.10655 | 0.10063 | 0.095333 | 0.090566 | 0.086253 | 0.082333 | 0.078753 | 0.075472 | 0.072453 | 0.069666 | 0.067086 | 0.06469 | 0.062459 | 0.060377 | 0.05843 | 0.056604 | 0.054889 | 0.053274 | 0.051752 | 0.050314 | 0.048955 | 0.047666 | 0.046444 | 0.045283
2700 | 0.88889 | 0.59259 | 0.44444 | 0.35556 | 0.2963 | 0.25397 | 0.22222 | 0.19753 | 0.17778 | 0.16162 | 0.14815 | 0.13675 | 0.12698 | 0.11852 | 0.11111 | 0.10458 | 0.098765 | 0.093567 | 0.088889 | 0.084656 | 0.080808 | 0.077295 | 0.074074 | 0.071111 | 0.068376 | 0.065844 | 0.063492 | 0.061303 | 0.059259 | 0.057348 | 0.055556 | 0.053872 | 0.052288 | 0.050794 | 0.049383 | 0.048048 | 0.046784 | 0.045584 | 0.044444
2750 | 0.87273 | 0.58182 | 0.43636 | 0.34909 | 0.29091 | 0.24935 | 0.21818 | 0.19394 | 0.17455 | 0.15868 | 0.14545 | 0.13427 | 0.12468 | 0.11636 | 0.10909 | 0.10267 | 0.09697 | 0.091866 | 0.087273 | 0.083117 | 0.079339 | 0.075889 | 0.072727 | 0.069818 | 0.067133 | 0.064646 | 0.062338 | 0.060188 | 0.058182 | 0.056305 | 0.054545 | 0.052893 | 0.051337 | 0.04987 | 0.048485 | 0.047174 | 0.045933 | 0.044755 | 0.043636
2800 | 0.85714 | 0.57143 | 0.42857 | 0.34286 | 0.28571 | 0.2449 | 0.21429 | 0.19048 | 0.17143 | 0.15584 | 0.14286 | 0.13187 | 0.12245 | 0.11429 | 0.10714 | 0.10084 | 0.095238 | 0.090226 | 0.085714 | 0.081633 | 0.077922 | 0.074534 | 0.071429 | 0.068571 | 0.065934 | 0.063492 | 0.061224 | 0.059113 | 0.057143 | 0.0553 | 0.053571 | 0.051948 | 0.05042 | 0.04898 | 0.047619 | 0.046332 | 0.045113 | 0.043956 | 0.042857
2850 | 0.84211 | 0.5614 | 0.42105 | 0.33684 | 0.2807 | 0.2406 | 0.21053 | 0.18713 | 0.16842 | 0.15311 | 0.14035 | 0.12955 | 0.1203 | 0.11228 | 0.10526 | 0.099071 | 0.093567 | 0.088643 | 0.084211 | 0.080201 | 0.076555 | 0.073227 | 0.070175 | 0.067368 | 0.064777 | 0.062378 | 0.06015 | 0.058076 | 0.05614 | 0.054329 | 0.052632 | 0.051037 | 0.049536 | 0.04812 | 0.046784 | 0.045519 | 0.044321 | 0.043185 | 0.042105
2900 | 0.82759 | 0.55172 | 0.41379 | 0.33103 | 0.27586 | 0.23645 | 0.2069 | 0.18391 | 0.16552 | 0.15047 | 0.13793 | 0.12732 | 0.11823 | 0.11034 | 0.10345 | 0.097363 | 0.091954 | 0.087114 | 0.082759 | 0.078818 | 0.075235 | 0.071964 | 0.068966 | 0.066207 | 0.06366 | 0.061303 | 0.059113 | 0.057075 | 0.055172 | 0.053393 | 0.051724 | 0.050157 | 0.048682 | 0.047291 | 0.045977 | 0.044734 | 0.043557 | 0.04244 | 0.041379
2950 | 0.81356 | 0.54237 | 0.40678 | 0.32542 | 0.27119 | 0.23245 | 0.20339 | 0.18079 | 0.16271 | 0.14792 | 0.13559 | 0.12516 | 0.11622 | 0.10847 | 0.10169 | 0.095713 | 0.090395 | 0.085638 | 0.081356 | 0.077482 | 0.07396 | 0.070744 | 0.067797 | 0.065085 | 0.062581 | 0.060264 | 0.058111 | 0.056108 | 0.054237 | 0.052488 | 0.050847 | 0.049307 | 0.047856 | 0.046489 | 0.045198 | 0.043976 | 0.042819 | 0.041721 | 0.040678
3000 | 0.8 | 0.53333 | 0.4 | 0.32 | 0.26667 | 0.22857 | 0.2 | 0.17778 | 0.16 | 0.14545 | 0.13333 | 0.12308 | 0.11429 | 0.10667 | 0.1 | 0.094118 | 0.088889 | 0.084211 | 0.08 | 0.07619 | 0.072727 | 0.069565 | 0.066667 | 0.064 | 0.061538 | 0.059259 | 0.057143 | 0.055172 | 0.053333 | 0.051613 | 0.05 | 0.048485 | 0.047059 | 0.045714 | 0.044444 | 0.043243 | 0.042105 | 0.041026 | 0.04
#VALUE! | $F$3 | #VALUE! | #VALUE! | #VALUE! | 53
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75
| Square | 70 | 75 | 80 | 85 | 90 | 95 | 100 | 110 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 225 | 250 | 275 | 300 | 325 | 350 | 375 | 400 | 425 | 450 | 475 | 500 | 525 | 550 | 575 | 600 | 625 | 650 | 675 | 700 | 725 | 750 | 775 | 800 | 825 | 850 | 875 | 900 | 925 | 950 | 975 | 1000 | 1050 | 1100 | 1150 | 1200 | 1250 | 1300 | 1350 | 1400 | 1450 | 1500 | 1550 | 1600 | 1650 | 1700 | 1750 | 1800 | 1850 | 1900 | 1950 | 2000 | 2050 | 2100 | 2150 | 2200 | 2250 | 2300
|  | 0.0038 | 0.0044 | 0.005 | 0.0057 | 0.0064 | 0.0071 | 0.0079 | 0.0095 | 0.0113 | 0.0133 | 0.0154 | 0.0177 | 0.0201 | 0.0227 | 0.0254 | 0.0284 | 0.0314 | 0.0398 | 0.0491 | 0.0594 | 0.0707 | 0.083 | 0.0962 | 0.1104 | 0.1257 | 0.1419 | 0.159 | 0.1772 | 0.1963 | 0.2165 | 0.2376 | 0.2597 | 0.2827 | 0.3068 | 0.3318 | 0.3578 | 0.3848 | 0.4128 | 0.4418 | 0.4717 | 0.5027 | 0.5346 | 0.5675 | 0.6013 | 0.6362 | 0.672 | 0.7088 | 0.7466 | 0.7854 | 0.8659 | 0.9503 | 1.0387 | 1.131 | 1.2272 | 1.3273 | 1.4314 | 1.5394 | 1.6513 | 1.7671 | 1.8869 | 2.0106 | 2.1382 | 2.2698 | 2.4053 | 2.5447 | 2.688 | 2.8353 | 2.9865 | 3.1416 | 3.3006 | 3.4636 | 2.6305 | 3.8013 | 3.9761 | 4.1548
1 | 0.015 | #VALUE! 1: 4.4; #VALUE! 2: 3.2; #VALUE! 3: 2.25; 53 4: 1.65; 53 5: 1.25; 53 6: 0.95; 53 7: 0.75; 53 8: 0.45; 53 9: 0.3; 53 10: 0.2; 53 11: 0.135
2 | 0.016 | #VALUE! 1: 5; #VALUE! 2: 3.8; #VALUE! 3: 2.6; 53 4: 1.9; 53 5: 1.4; 53 6: 1.05; 53 7: 0.85; 53 8: 0.5; 53 9: 0.33; 53 10: 0.22; 53 11: 0.15; 53 12: 0.105
3 | 0.017 | #VALUE! 1: 5.5; #VALUE! 2: 4; #VALUE! 3: 2.9; 53 4: 2.1; 53 5: 1.6; 53 6: 1.2; 53 7: 0.95; 53 8: 0.55; 53 9: 0.37; 53 10: 0.24; 53 11: 0.17; 53 12: 0.12
4 | 0.018 | #VALUE! 1: 6; #VALUE! 2: 4.5; #VALUE! 3: 3.2; 53 4: 2.4; 53 5: 1.8; 53 6: 1.35; 53 7: 1.05; 53 8: 6.5; 53 9: 0.425; 53 10: 0.27; 53 11: 0.19; 53 12: 0.135; 53 13: 0.1
5 | 0.019 | #VALUE! 1: 7; #VALUE! 2: 5; #VALUE! 3: 3.6; 53 4: 2.6; 53 5: 2; 53 6: 1.5; 53 7: 1.175; 53 8: 0.7; 53 9: 0.46; 53 10: 0.3; 53 11: 0.21; 53 12: 0.15; 53 13: 0.11
6 | 0.02 | #VALUE! 1: 7.5; #VALUE! 2: 5.5; #VALUE! 3: 4; 53 4: 2.95; 53 5: 2.2; 53 6: 1.6; 53 7: 1.3; 53 8: 0.75; 53 9: 0.5; 53 10: 0.33; 53 11: 0.23; 53 12: 0.16; 53 13: 0.12
7 | 0.021 | #VALUE! 1: 8.25; #VALUE! 2: 6; #VALUE! 3: 4.4; 53 4: 3.1; 53 5: 2.4; 53 6: 1.8; 53 7: 1.4; 53 8: 0.85; 53 9: 0.55; 53 10: 0.36; 53 11: 0.25; 53 12: 0.18; 53 13: 0.13
8 | 0.022 | #VALUE! 1: 9; #VALUE! 2: 6.5; #VALUE! 3: 4.75; 53 4: 3.4; 53 5: 2.6; 53 6: 2; 53 7: 1.55; 53 8: 0.9; 53 9: 0.6; 53 10: 0.4; 53 11: 0.28; 53 12: 0.2; 53 13: 0.14; 53 14: 0.105
9 | 0.023 | #VALUE! 1: 10; #VALUE! 2: 7; #VALUE! 3: 5.1; 53 4: 3.9; 53 5: 2.8; 53 6: 2.1; 53 7: 1.65; 53 8: 1; 53 9: 0.65; 53 10: 0.44; 53 11: 0.3; 53 12: 0.22; 53 13: 0.155; 53 14: 0.115
10 | 0.024 | #VALUE! 1: 11; #VALUE! 2: 7.5; #VALUE! 3: 5.6; 53 4: 4; 53 5: 3; 53 6: 2.3; 53 7: 1.8; 53 8: 1.1; 53 9: 0.7; 53 10: 0.48; 53 11: 0.32; 53 12: 0.24; 53 13: 0.17; 53 14: 0.125
11 | 0.025 | #VALUE! 1: 11.5; #VALUE! 2: 8; #VALUE! 3: 6; 53 4: 4.4; 53 5: 3.2; 53 6: 2.5; 53 7: 1.95; 53 8: 1.2; 53 9: 0.75; 53 10: 0.525; 53 11: 0.35; 53 12: 0.26; 53 13: 0.18; 53 14: 0.13; 53 15: 0.1
12 | 0.026 | #VALUE! 1: 12.5; #VALUE! 2: 8.75; #VALUE! 3: 6.5; 53 4: 4.72; 53 5: 3.6; 53 6: 2.7; 53 7: 2.1; 53 8: 1.3; 53 9: 0.85; 53 10: 0.55; 53 11: 0.38; 53 12: 0.28; 53 13: 0.2; 53 14: 0.145; 53 15: 0.11
13 | 0.027 | #VALUE! 1: 13.5; #VALUE! 2: 9.5; #VALUE! 3: 7; 53 4: 5.04; 53 5: 3.8; 53 6: 2.9; 53 7: 2.2; 53 8: 1.4; 53 9: 0.9; 53 10: 0.6; 53 11: 0.4; 53 12: 0.3; 53 13: 0.21; 53 14: 0.15; 53 15: 0.115
14 | 0.028 | #VALUE! 1: 14.5; #VALUE! 2: 10.25; #VALUE! 3: 7.5; 53 4: 5.36; 53 5: 4; 53 6: 3.1; 53 7: 2.4; 53 8: 1.5; 53 9: 0.95; 53 10: 0.65; 53 11: 0.425; 53 12: 0.32; 53 13: 0.23; 53 14: 0.16; 53 15: 0.125
15 | 0.029 | #VALUE! 1: 15.5; #VALUE! 2: 10.75; #VALUE! 3: 8; 53 4: 5.68; 53 5: 4.25; 53 6: 3.3; 53 7: 2.6; 53 8: 1.6; 53 9: 1; 53 10: 0.7; 53 11: 0.475; 53 12: 0.34; 53 13: 0.24; 53 14: 0.17; 53 15: 0.13; 53 16: 0.1
16 | 0.03 | #VALUE! 1: 16; #VALUE! 2: 11.25; #VALUE! 3: 8.5; 53 4: 6; 53 5: 4.5; 53 6: 3.4; 53 7: 2.7; 53 8: 1.7; 53 9: 1.1; 53 10: 0.725; 53 11: 0.5; 53 12: 0.36; 53 13: 0.25; 53 14: 0.18; 53 15: 0.14; 53 16: 0.11
17 | 0.032 | #VALUE! 1: 18.5; #VALUE! 2: 12.5; #VALUE! 3: 9.5; 53 4: 7; 53 5: 5.25; 53 6: 4; 53 7: 3.05; 53 8: 1.85; 53 9: 1.2; 53 10: 0.8; 53 11: 0.55; 53 12: 0.4; 53 13: 0.28; 53 14: 0.2; 53 15: 0.16; 53 16: 0.12
18 | 0.034 | #VALUE! 1: 20.5; #VALUE! 2: 14; #VALUE! 3: 10.75; 53 4: 8; 53 5: 6; 53 6: 4.4; 53 7: 3.4; 53 8: 2.1; 53 9: 1.4; 53 10: 0.9; 53 11: 0.6; 53 12: 0.45; 53 13: 0.32; 53 14: 0.23; 53 15: 0.175; 53 16: 0.14; 53 17: 0.1
19 | 0.036 | #VALUE! 1: 23; #VALUE! 2: 16; #VALUE! 3: 12; 53 4: 8.75; 53 5: 6.5; 53 6: 5; 53 7: 3.8; 53 8: 2.3; 53 9: 1.55; 53 10: 1; 53 11: 0.7; 53 12: 0.5; 53 13: 0.36; 53 14: 0.25; 53 15: 0.2; 53 16: 0.15; 53 17: 0.11
20 | 0.038 | #VALUE! 1: 26; #VALUE! 2: 18; #VALUE! 3: 13.5; 53 4: 9.5; 53 5: 7.25; 53 6: 5.5; 53 7: 4.25; 53 8: 2.6; 53 9: 1.7; 53 10: 1.1; 53 11: 0.75; 53 12: 0.55; 53 13: 0.4; 53 14: 0.28; 53 15: 0.22; 53 16: 0.17; 53 17: 0.12
21 | 0.04 | #VALUE! 1: 28; #VALUE! 2: 20; #VALUE! 3: 15; 53 4: 10.75; 53 5: 8; 53 6: 6; 53 7: 4.5; 53 8: 2.9; 53 9: 1.85; 53 10: 1.2; 53 11: 0.85; 53 12: 0.6; 53 13: 0.45; 53 14: 0.31; 53 15: 0.24; 53 16: 0.185; 53 17: 0.14
22 | 0.042 | #VALUE! 1: 31; #VALUE! 2: 22; #VALUE! 3: 16.5; 53 4: 12; 53 5: 8.75; 53 6: 6.5; 53 7: 5.25; 53 8: 3.1; 53 9: 2; 53 10: 1.35; 53 11: 0.9; 53 12: 0.67; 53 13: 0.5; 53 14: 0.34; 53 15: 0.26; 53 16: 0.2; 53 17: 0.155
23 | 0.044 | #VALUE! 1: 34; #VALUE! 2: 24; #VALUE! 3: 18; 53 4: 13; 53 5: 9.5; 53 6: 7.25; 53 7: 5.5; 53 8: 3.4; 53 9: 2.2; 53 10: 1.45; 53 11: 1; 53 12: 0.74; 53 13: 0.54; 53 14: 0.36; 53 15: 0.28; 53 16: 0.22; 53 17: 0.17
24 | 0.046 | #VALUE! 1: 36; #VALUE! 2: 26; #VALUE! 3: 19.5; 53 4: 14; 53 5: 10.25; 53 6: 7.75; 53 7: 6; 53 8: 3.7; 53 9: 2.4; 53 10: 1.55; 53 11: 1.1; 53 12: 0.8; 53 13: 0.57; 53 14: 0.4; 53 15: 0.31; 53 16: 0.24; 53 17: 0.185; 53 18: 0.1
25 | 0.048 | #VALUE! 1: 40; #VALUE! 2: 28; #VALUE! 3: 21; 53 4: 15; 53 5: 11; 53 6: 8.5; 53 7: 6.5; 53 8: 4; 53 9: 2.6; 53 10: 1.7; 53 11: 1.4; 53 12: 0.85; 53 13: 0.625; 53 14: 0.44; 53 15: 0.34; 53 16: 0.26; 53 17: 0.2; 53 18: 0.11
26 | 0.05 | #VALUE! 1: 42.5; #VALUE! 2: 31; #VALUE! 3: 22.5; 53 4: 16; 53 5: 12; 53 6: 9; 53 7: 7; 53 8: 4.25; 53 9: 2.8; 53 10: 1.8; 53 11: 1.6; 53 12: 0.95; 53 13: 0.66; 53 14: 0.46; 53 15: 0.36; 53 16: 0.28; 53 17: 0.22; 53 18: 0.115
27 | 0.052 | #VALUE! 1: 46; #VALUE! 2: 33; #VALUE! 3: 24; 53 4: 17.5; 53 5: 13; 53 6: 10; 53 7: 7.5; 53 8: 4.5; 53 9: 3.1; 53 10: 2; 53 11: 1.4; 53 12: 1; 53 13: 0.72; 53 14: 0.5; 53 15: 0.39; 53 16: 0.3; 53 17: 0.23; 53 18: 0.125
28 | 0.054 | #VALUE! 1: 49; #VALUE! 2: 36; #VALUE! 3: 26; 53 4: 19; 53 5: 14; 53 6: 10.5; 53 7: 8; 53 8: 5; 53 9: 3.15; 53 10: 2.1; 53 11: 1.5; 53 12: 1.1; 53 13: 0.77; 53 14: 0.54; 53 15: 0.425; 53 16: 0.32; 53 17: 0.25; 53 18: 0.13
29 | 0.056 | #VALUE! 1: 52.5; #VALUE! 2: 39; #VALUE! 3: 29; 53 4: 20; 53 5: 15; 53 6: 11.5; 53 7: 8.5; 53 8: 5.25; 53 9: 3.6; 53 10: 2.3; 53 11: 1.6; 53 12: 1.15; 53 13: 0.85; 53 14: 0.57; 53 15: 0.45; 53 16: 0.33; 53 17: 0.27; 53 18: 0.14
30 | 0.058 | #VALUE! 1: 57.5; #VALUE! 2: 41; #VALUE! 3: 30; 53 4: 21; 53 5: 16; 53 6: 12; 53 7: 9.5; 53 8: 5.5; 53 9: 3.8; 53 10: 2.4; 53 11: 1.7; 53 12: 1.2; 53 13: 0.9; 53 14: 0.6; 53 15: 0.475; 53 16: 0.37; 53 17: 0.28; 53 18: 0.15
31 | 0.06 | #VALUE! 1: 60; #VALUE! 2: 44; #VALUE! 3: 32; 53 4: 23; 53 5: 17; 53 6: 13; 53 7: 10; 53 8: 6; 53 9: 4; 53 10: 2.6; 53 11: 1.8; 53 12: 1.3; 53 13: 0.95; 53 14: 0.65; 53 15: 0.5; 53 16: 0.4; 53 17: 0.3; 53 18: 0.16; 53 19: 0.1
32 | 0.065 | #VALUE! 1: 70; #VALUE! 2: 52; #VALUE! 3: 37; 53 4: 28.5; 53 5: 20; 53 6: 15; 53 7: 11.5; 53 8: 7; 53 9: 4.6; 53 10: 3; 53 11: 2.1; 53 12: 1.5; 53 13: 1.1; 53 14: 0.75; 53 15: 0.7; 53 16: 0.46; 53 17: 0.36; 53 18: 0.19; 53 19: 0.115
33 | 0.07 | #VALUE! 1: 80; #VALUE! 2: 60; #VALUE! 3: 42.5; 53 4: 31; 53 5: 23; 53 6: 17.5; 53 7: 13.5; 53 8: 8; 53 9: 5.4; 53 10: 3.5; 53 11: 2.4; 53 12: 1.75; 53 13: 1.3; 53 14: 0.9; 53 15: 0.7; 53 16: 0.53; 53 17: 0.4; 53 18: 0.22; 53 19: 0.13
34 | 0.075 | #VALUE! 2: 67.5; #VALUE! 3: 50; 53 4: 35; 53 5: 26; 53 6: 20; 53 7: 15; 53 8: 9; 53 9: 6; 53 10: 4; 53 11: 2.8; 53 12: 2; 53 13: 1.45; 53 14: 1; 53 15: 0.6; 53 16: 0.6; 53 17: 0.46; 53 18: 0.245; 53 19: 0.15
35 | 0.08 | #VALUE! 2: 77.5; #VALUE! 3: 55; 53 4: 40; 53 5: 29; 53 6: 22; 53 7: 17.5; 53 8: 10.5; 53 9: 7; 53 10: 4.5; 53 11: 3.1; 53 12: 2.2; 53 13: 1.65; 53 14: 1.15; 53 15: 0.8; 53 16: 0.7; 53 17: 0.54; 53 18: 0.28; 53 19: 0.17; 53 20: 0.1
36 | 0.085 | #VALUE! 3: 62.5; 53 4: 45; 53 5: 33; 53 6: 25; 53 7: 20; 53 8: 11.5; 53 9: 7.75; 53 10: 5; 53 11: 3.5; 53 12: 2.5; 53 13: 1.8; 53 14: 1.3; 53 15: 1; 53 16: 0.75; 53 17: 0.6; 53 18: 0.31; 53 19: 0.19; 53 20: 0.115
37 | 0.09 | #VALUE! 3: 70; 53 4: 50; 53 5: 36; 53 6: 28; 53 7: 22; 53 8: 13; 53 9: 8.5; 53 10: 5.5; 53 11: 4; 53 12: 2.8; 53 13: 2; 53 14: 1.4; 53 15: 1.1; 53 16: 0.85; 53 17: 0.65; 53 18: 0.35; 53 19: 0.21; 53 20: 0.125
38 | 0.095 | #VALUE! 3: 77.5; 53 4: 56; 53 5: 40; 53 6: 31; 53 7: 24; 53 8: 14; 53 9: 9.5; 53 10: 6; 53 11: 4.5; 53 12: 3.1; 53 13: 2.2; 53 14: 1.6; 53 15: 1.2; 53 16: 0.95; 53 17: 0.73; 53 18: 0.38; 53 19: 0.23; 53 20: 0.14
39 | 0.1 | #VALUE! 3: 85; 53 4: 62.5; 53 5: 45; 53 6: 34; 53 7: 26; 53 8: 16; 53 9: 10.5; 53 10: 7; 53 11: 5; 53 12: 3.4; 53 13: 2.4; 53 14: 1.7; 53 15: 1.4; 53 16: 1.05; 53 17: 0.8; 53 18: 0.425; 53 19: 0.24; 53 20: 0.15; 53 21: 0.1
40 | 0.11 | 53 4: 75; 53 5: 55; 53 6: 42.5; 53 7: 32; 53 8: 20; 53 9: 13; 53 10: 8.5; 53 11: 6; 53 12: 4; 53 13: 3; 53 14: 2.1; 53 15: 1.65; 53 16: 1.3; 53 17: 0.95; 53 18: 0.5; 53 19: 0.3; 53 20: 0.19; 53 21: 0.12
41 | 0.12 | 53 5: 65; 53 6: 47.5; 53 7: 38; 53 8: 23; 53 9: 15; 53 10: 10; 53 11: 7; 53 12: 4.7; 53 13: 3.5; 53 14: 2.4; 53 15: 1.9; 53 16: 1.5; 53 17: 1.1; 53 18: 0.6; 53 19: 0.36; 53 20: 0.22; 53 21: 0.14; 53 22: 0.1
42 | 0.13 | 53 5: 75; 53 6: 57.5; 53 7: 44; 53 8: 27; 53 9: 17; 53 10: 11.5; 53 11: 8; 53 12: 5.5; 53 13: 4; 53 14: 2.8; 53 15: 2.2; 53 16: 1.75; 53 17: 1.3; 53 18: 0.7; 53 19: 0.42; 53 20: 0.25; 53 21: 0.165; 53 22: 0.12
43 | 0.14 | 53 6: 65; 53 7: 50; 53 8: 31; 53 9: 20; 53 10: 13; 53 11: 9.5; 53 12: 6.4; 53 13: 4.5; 53 14: 3.2; 53 15: 2.6; 53 16: 2; 53 17: 1.5; 53 18: 0.8; 53 19: 0.475; 53 20: 0.3; 53 21: 0.19; 53 22: 0.16
44 | 0.15 | 53 6: 75; 53 7: 57.5; 53 8: 36; 53 9: 24; 53 10: 15; 53 11: 11; 53 12: 7.25; 53 13: 5.25; 53 14: 3.7; 53 15: 3; 53 16: 2.3; 53 17: 1.75; 53 18: 0.9; 53 19: 0.55; 53 20: 0.34; 53 21: 0.22; 53 22: 0.15; 53 23: 0.1
45 | 0.16 | 53 7: 66; 53 8: 40; 53 9: 26; 53 10: 17; 53 11: 12; 53 12: 8.25; 53 13: 6; 53 14: 4.25; 53 15: 3.3; 53 16: 2.6; 53 17: 1.95; 53 18: 1; 53 19: 0.625; 53 20: 0.38; 53 21: 0.24; 53 22: 0.17; 53 23: 0.115
46 | 0.17 | 53 7: 75; 53 8: 45; 53 9: 30; 53 10: 19; 53 11: 14; 53 12: 9.25; 53 13: 6.75; 53 14: 4.6; 53 15: 3.7; 53 16: 2.9; 53 17: 2.2; 53 18: 1.15; 53 19: 0.7; 53 20: 0.425; 53 21: 0.28; 53 22: 0.19; 53 23: 0.13
47 | 0.18 | 53 8: 50; 53 9: 33; 53 10: 21; 53 11: 15; 53 12: 10.5; 53 13: 7.5; 53 14: 5.25; 53 15: 4.1; 53 16: 3.2; 53 17: 2.4; 53 18: 1.3; 53 19: 0.77; 53 20: 0.475; 53 21: 0.3; 53 22: 0.21; 53 23: 0.145; 53 24: 0.1
48 | 0.19 | 53 8: 55; 53 9: 36; 53 10: 24; 53 11: 17; 53 12: 11.5; 53 13: 8.5; 53 14: 5.75; 53 15: 4.5; 53 16: 3.6; 53 17: 2.7; 53 18: 1.4; 53 19: 0.85; 53 20: 0.525; 53 21: 0.34; 53 22: 0.23; 53 23: 0.16; 53 24: 0.11
49 | 0.2 | 53 8: 60; 53 9: 40; 53 10: 27; 53 11: 18.5; 53 12: 12.5; 53 13: 9; 53 14: 6.25; 53 15: 5; 53 16: 4; 53 17: 3; 53 18: 1.55; 53 19: 0.95; 53 20: 0.6; 53 21: 0.38; 53 22: 0.26; 53 23: 0.175; 53 24: 0.14
50 | 0.21 | 53 8: 65; 53 9: 44; 53 10: 30; 53 11: 20.5; 53 12: 14; 53 13: 10; 53 14: 7; 53 15: 5.5; 53 16: 4.4; 53 17: 3.2; 53 18: 1.7; 53 19: 1.05; 53 20: 0.65; 53 21: 0.4; 53 22: 0.28; 53 23: 0.19; 53 24: 0.13; 53 25: 0.1
51 | 0.22 | 53 8: 72.5; 53 9: 48; 53 10: 33; 53 11: 23; 53 12: 15; 53 13: 11; 53 14: 7.5; 53 15: 6; 53 16: 4.7; 53 17: 3.6; 53 18: 1.9; 53 19: 1.15; 53 20: 0.7; 53 21: 0.44; 53 22: 0.3; 53 23: 0.21; 53 24: 0.14; 53 25: 0.11
52 | 0.23 | 53 8: 80; 53 9: 52; 53 10: 36; 53 11: 25; 53 12: 16.5; 53 13: 12; 53 14: 8; 53 15: 6.5; 53 16: 5.3; 53 17: 3.9; 53 18: 2; 53 19: 1.25; 53 20: 0.75; 53 21: 0.475; 53 22: 0.34; 53 23: 0.23; 53 24: 0.16; 53 25: 0.12
53 | 0.24 | 53 9: 56; 53 10: 38; 53 11: 27; 53 12: 18; 53 13: 13; 53 14: 9; 53 15: 7; 53 16: 5.7; 53 17: 4.2; 53 18: 2.2; 53 19: 1.35; 53 20: 0.85; 53 21: 0.52; 53 22: 0.36; 53 23: 0.26; 53 24: 0.17; 53 25: 0.13
54 | 0.25 | 53 9: 60; 53 10: 42; 53 11: 29; 53 12: 19; 53 13: 14; 53 14: 9.5; 53 15: 7.5; 53 16: 6; 53 17: 4.5; 53 18: 2.4; 53 19: 1.45; 53 20: 0.9; 53 21: 0.55; 53 22: 0.39; 53 23: 0.27; 53 24: 0.185; 53 25: 0.14; 53 26: 0.1
55 | 0.26 | 53 9: 65; 53 10: 45; 53 11: 31; 53 12: 21; 53 13: 15; 53 14: 11; 53 15: 8.5; 53 16: 6.5; 53 17: 4.8; 53 18: 2.6; 53 19: 1.6; 53 20: 1; 53 21: 0.6; 53 22: 0.425; 53 23: 0.295; 53 24: 0.2; 53 25: 0.15; 53 26: 0.11
56 | 0.27 | 53 9: 70; 53 10: 48; 53 11: 33; 53 12: 22; 53 13: 16; 53 14: 12; 53 15: 9; 53 16: 7; 53 17: 5.3; 53 18: 2.8; 53 19: 1.7; 53 20: 1.05; 53 21: 0.65; 53 22: 0.45; 53 23: 0.31; 53 24: 0.22; 53 25: 0.16; 53 26: 0.115
57 | 0.28 | 53 9: 75; 53 10: 50; 53 11: 36; 53 12: 24; 53 13: 18; 53 14: 13; 53 15: 9.5; 53 16: 7.5; 53 17: 5.5; 53 18: 3; 53 19: 1.8; 53 20: 1.1; 53 21: 0.7; 53 22: 0.475; 53 23: 0.34; 53 24: 0.23; 53 25: 0.17; 53 26: 0.125
58 | 0.29 | 53 9: 80; 53 10: 55; 53 11: 38; 53 12: 26; 53 13: 19; 53 14: 14; 53 15: 10.5; 53 16: 8; 53 17: 6; 53 18: 3.2; 53 19: 1.9; 53 20: 1.2; 53 21: 0.75; 53 22: 0.525; 53 23: 0.36; 53 24: 0.24; 53 25: 0.185; 53 26: 0.135; 53 27: 0.1
59 | 0.3 | 53 10: 60; 53 11: 40; 53 12: 28; 53 13: 20; 53 14: 15; 53 15: 11; 53 16: 8.7; 53 17: 6.4; 53 18: 3.3; 53 19: 2; 53 20: 1.3; 53 21: 0.8; 53 22: 0.55; 53 23: 0.38; 53 24: 0.26; 53 25: 0.2; 53 26: 0.14; 53 27: 0.105
60 | 0.32 | 53 10: 65; 53 11: 45; 53 12: 32; 53 13: 23; 53 14: 17; 53 15: 12.5; 53 16: 10; 53 17: 7; 53 18: 3.9; 53 19: 2.3; 53 20: 1.45; 53 21: 0.9; 53 22: 0.6; 53 23: 0.425; 53 24: 0.3; 53 25: 0.22; 53 26: 0.16; 53 27: 0.12
61 | 0.34 | 53 10: 75; 53 11: 52; 53 12: 36; 53 13: 26; 53 14: 19; 53 15: 14; 53 16: 11; 53 17: 8; 53 18: 4.25; 53 19: 2.6; 53 20: 1.65; 53 21: 1; 53 22: 0.7; 53 23: 0.48; 53 24: 0.34; 53 25: 0.25; 53 26: 0.18; 53 27: 0.14; 53 28: 0.1
62 | 0.36 | 53 10: 80; 53 11: 57; 53 12: 40; 53 13: 29; 53 14: 21; 53 15: 15.5; 53 16: 12.5; 53 17: 9; 53 18: 4.75; 53 19: 2.9; 53 20: 1.8; 53 21: 1.1; 53 22: 0.8; 53 23: 0.55; 53 24: 0.38; 53 25: 0.28; 53 26: 0.2; 53 27: 0.15; 53 28: 0.11
63 | 0.38 | 53 11: 64; 53 12: 45; 53 13: 32; 53 14: 24; 53 15: 18; 53 16: 14; 53 17: 10; 53 18: 5.3; 53 19: 3.2; 53 20: 2; 53 21: 1.25; 53 22: 0.9; 53 23: 0.6; 53 24: 0.4; 53 25: 0.32; 53 26: 0.22; 53 27: 0.17; 53 28: 0.125; 53 29: 0.1
64 | 0.4 | 53 11: 70; 53 12: 50; 53 13: 35; 53 14: 26; 53 15: 19; 53 16: 15; 53 17: 11; 53 18: 6; 53 19: 3.6; 53 20: 2.2; 53 21: 1.4; 53 22: 1; 53 23: 0.65; 53 24: 0.45; 53 25: 0.35; 53 26: 0.24; 53 27: 0.18; 53 28: 0.14; 53 29: 0.11
65 | 0.42 | 53 11: 76; 53 12: 55; 53 13: 39; 53 14: 28; 53 15: 21; 53 16: 16.5; 53 17: 12; 53 18: 6.5; 53 19: 3.9; 53 20: 2.4; 53 21: 1.5; 53 22: 1.05; 53 23: 0.7; 53 24: 0.48; 53 25: 0.38; 53 26: 0.26; 53 27: 0.2; 53 28: 0.15; 53 29: 0.12
66 | 0.44 | 53 11: 82; 53 12: 60; 53 13: 43; 53 14: 31; 53 15: 23; 53 16: 18.5; 53 17: 13; 53 18: 7; 53 19: 4.25; 53 20: 2.6; 53 21: 1.65; 53 22: 1.2; 53 23: 0.8; 53 24: 0.55; 53 25: 0.425; 53 26: 0.3; 53 27: 2.2; 53 28: 0.165; 53 29: 0.13
67 | 0.46 | 53 12: 65; 53 13: 46; 53 14: 34; 53 15: 25; 53 16: 20; 53 17: 14; 53 18: 7.5; 53 19: 4.5; 53 20: 2.95; 53 21: 1.8; 53 22: 1.3; 53 23: 0.85; 53 24: 0.6; 53 25: 0.45; 53 26: 0.32; 53 27: 2.4; 53 28: 0.18; 53 29: 0.14; 53 30: 0.1
68 | 0.48 | 53 12: 70; 53 13: 50; 53 14: 36; 53 15: 28; 53 16: 22; 53 17: 15.5; 53 18: 8.5; 53 19: 5; 53 20: 3.1; 53 21: 1.95; 53 22: 1.4; 53 23: 0.9; 53 24: 0.65; 53 25: 0.5; 53 26: 0.35; 53 27: 2.6; 53 28: 0.2; 53 29: 0.15; 53 30: 0.11
69 | 0.5 | 53 12: 75; 53 13: 54; 53 14: 40; 53 15: 30; 53 16: 23; 53 17: 16.5; 53 18: 9; 53 19: 5.25; 53 20: 3.4; 53 21: 2.1; 53 22: 1.5; 53 23: 1; 53 24: 0.7; 53 25: 0.55; 53 26: 0.38; 53 27: 2.8; 53 28: 0.21; 53 29: 0.165; 53 30: 0.12; 53 31: 0.1
70 | 0.52 | 53 12: 80; 53 13: 58; 53 14: 42.5; 53 15: 31; 53 16: 25; 53 17: 18; 53 18: 9.75; 53 19: 5.75; 53 20: 3.6; 53 21: 2.3; 53 22: 1.6; 53 23: 1.1; 53 24: 0.75; 53 25: 0.6; 53 26: 0.42; 53 27: 0.3; 53 28: 0.23; 53 29: 0.175; 53 30: 0.13; 53 31: 0.105
71 | 0.54 | 53 13: 62; 53 14: 46; 53 15: 34; 53 16: 27; 53 17: 19.5; 53 18: 10.5; 53 19: 6.25; 53 20: 4; 53 21: 2.4; 53 22: 1.7; 53 23: 1.2; 53 24: 0.8; 53 25: 0.65; 53 26: 0.45; 53 27: 0.33; 53 28: 0.25; 53 29: 0.18; 53 30: 0.14; 53 31: 0.115; 53 32: 0.1
72 | 0.56 | 53 13: 66; 53 14: 50; 53 15: 36; 53 16: 29; 53 17: 21; 53 18: 11; 53 19: 6.5; 53 20: 4.25; 53 21: 2.6; 53 22: 1.8; 53 23: 1.3; 53 24: 0.9; 53 25: 0.7; 53 26: 0.475; 53 27: 0.35; 53 28: 0.265; 53 29: 0.2; 53 30: 0.15; 53 31: 0.125; 53 32: 0.105
73 | 0.58 | 53 13: 70; 53 14: 52.5; 53 15: 38; 53 16: 32; 53 17: 22; 53 18: 12; 53 19: 7; 53 20: 4.5; 53 21: 2.8; 53 22: 2; 53 23: 1.4; 53 24: 0.95; 53 25: 0.75; 53 26: 0.5; 53 27: 0.38; 53 28: 0.28; 53 29: 0.21; 53 30: 0.16; 53 31: 0.135; 53 32: 0.115
74 | 0.6 | 53 13: 75; 53 14: 55; 53 15: 40; 53 16: 33; 53 17: 24; 53 18: 12.5; 53 19: 7.5; 53 20: 4.75; 53 21: 3; 53 22: 2.1; 53 23: 1.5; 53 24: 1; 53 25: 0.8; 53 26: 0.54; 53 27: 0.4; 53 28: 0.3; 53 29: 0.23; 53 30: 0.17; 53 31: 0.14; 53 32: 0.12; 53 33: 0.1
75 | 0.65 | 53 14: 65; 53 15: 47; 53 16: 39; 53 17: 28; 53 18: 15; 53 19: 8.75; 53 20: 5.5; 53 21: 3.5; 53 22: 2.5; 53 23: 1.75; 53 24: 1.2; 53 25: 0.9; 53 26: 0.625; 53 27: 0.47; 53 28: 0.35; 53 29: 0.27; 53 30: 0.2; 53 31: 0.16; 53 32: 0.14; 53 33: 0.115
76 | 0.7 | 53 14: 75; 53 15: 55; 53 16: 45; 53 17: 32; 53 18: 17; 53 19: 10; 53 20: 6.5; 53 21: 4; 53 22: 2.9; 53 23: 2; 53 24: 0.14; 53 25: 1; 53 26: 0.7; 53 27: 0.53; 53 28: 0.4; 53 29: 0.3; 53 30: 0.23; 53 31: 0.19; 53 32: 0.16; 53 33: 0.13; 53 34: 0.1
77 | 0.75 | 53 15: 65; 53 16: 50; 53 17: 37; 53 18: 19; 53 19: 11.5; 53 20: 7.25; 53 21: 4.5; 53 22: 3.2; 53 23: 2.3; 53 24: 1.55; 53 25: 1.15; 53 26: 0.8; 53 27: 0.62; 53 28: 0.46; 53 29: 0.35; 53 30: 0.26; 53 31: 0.21; 53 32: 0.18; 53 33: 0.15; 53 34: 0.115; 53 35: 0.1
78 | 0.8 | 53 15: 70; 53 16: 57; 53 17: 40; 53 18: 22; 53 19: 13; 53 20: 8; 53 21: 5; 53 22: 3.7; 53 23: 2.6; 53 24: 1.8; 53 25: 1.3; 53 26: 0.9; 53 27: 0.7; 53 28: 0.525; 53 29: 0.4; 53 30: 0.3; 53 31: 0.24; 53 32: 0.21; 53 33: 0.17; 53 34: 0.13; 53 35: 0.11
79 | 0.85 | 53 15: 80; 53 16: 65; 53 17: 46; 53 18: 25; 53 19: 14.5; 53 20: 9.25; 53 21: 6; 53 22: 4.25; 53 23: 2.9; 53 24: 2; 53 25: 1.5; 53 26: 1; 53 27: 0.8; 53 28: 0.6; 53 29: 0.45; 53 30: 0.34; 53 31: 0.27; 53 32: 0.24; 53 33: 0.195; 53 34: 0.145; 53 35: 0.125; 53 36: 0.1
80 | 0.9 | 53 16: 72; 53 17: 50; 53 18: 28; 53 19: 16; 53 20: 10; 53 21: 6.5; 53 22: 4.5; 53 23: 3.2; 53 24: 2.2; 53 25: 1.6; 53 26: 1.1; 53 27: 0.9; 53 28: 0.65; 53 29: 0.5; 53 30: 0.37; 53 31: 0.3; 53 32: 0.26; 53 33: 0.2175; 53 34: 0.16; 53 35: 0.14; 53 36: 0.11
81 | 0.95 | 53 16: 80; 53 17: 57; 53 18: 30; 53 19: 18; 53 20: 11; 53 21: 7; 53 22: 4.75; 53 23: 3.5; 53 24: 2.5; 53 25: 1.85; 53 26: 1.25; 53 27: 1; 53 28: 0.725; 53 29: 0.55; 53 30: 0.42; 53 31: 0.34; 53 32: 0.3; 53 33: 0.24; 53 34: 0.18; 53 35: 0.15; 53 36: 0.125; 53 37: 0.1
82 | 1 | 53 17: 63; 53 18: 34; 53 19: 20; 53 20: 12; 53 21: 8; 53 22: 5.6; 53 23: 4; 53 24: 2.7; 53 25: 2; 53 26: 1.4; 53 27: 1.1; 53 28: 0.8; 53 29: 0.6; 53 30: 0.45; 53 31: 0.37; 53 32: 0.32; 53 33: 0.26; 53 34: 0.2; 53 35: 0.165; 53 36: 0.14; 53 37: 0.11; 53 38: 0.1
83 | 1.1 | 53 17: 76; 53 18: 40; 53 19: 24; 53 20: 14.5; 53 21: 9.5; 53 22: 7; 53 23: 4.7; 53 24: 3.2; 53 25: 2.4; 53 26: 1.6; 53 27: 1.3; 53 28: 0.95; 53 29: 0.75; 53 30: 0.54; 53 31: 0.45; 53 32: 0.4; 53 33: 0.32; 53 34: 0.24; 53 35: 0.2; 53 36: 0.165; 53 37: 0.13; 53 38: 0.12; 53 39: 0.1
84 | 1.2 | 53 18: 47.5; 53 19: 28; 53 20: 17; 53 21: 11.25; 53 22: 8; 53 23: 5.5; 53 24: 3.8; 53 25: 2.8; 53 26: 1.9; 53 27: 1.5; 53 28: 1.15; 53 29: 0.85; 53 30: 0.625; 53 31: 0.525; 53 32: 0.45; 53 33: 0.38; 53 34: 0.28; 53 35: 0.24; 53 36: 0.2; 53 37: 0.155; 53 38: 0.14; 53 39: 0.115; 53 40: 0.1
85 | 1.3 | 53 18: 55; 53 19: 32; 53 20: 20; 53 21: 13; 53 22: 9.5; 53 23: 6.5; 53 24: 4.5; 53 25: 3.3; 53 26: 2.2; 53 27: 1.75; 53 28: 1.35; 53 29: 1; 53 30: 0.75; 53 31: 0.6; 53 32: 0.525; 53 33: 0.44; 53 34: 0.33; 53 35: 0.28; 53 36: 0.23; 53 37: 0.18; 53 38: 0.165; 53 39: 0.135; 53 40: 0.115; 53 41: 0.1
86 | 1.4 | 53 18: 65; 53 19: 38; 53 20: 23; 53 21: 15; 53 22: 11; 53 23: 7.5; 53 24: 5; 53 25: 3.8; 53 26: 2.6; 53 27: 2; 53 28: 1.55; 53 29: 1.15; 53 30: 0.85; 53 31: 0.7; 53 32: 0.6; 53 33: 0.5; 53 34: 0.38; 53 35: 0.32; 53 36: 0.26; 53 37: 0.21; 53 38: 0.19; 53 39: 0.155; 53 40: 0.135; 53 41: 0.115; 53 42: 0.1
87 | 1.5 | 53 18: 74; 53 19: 42.5; 53 20: 26; 53 21: 17.5; 53 22: 12; 53 23: 8.5; 53 24: 6; 53 25: 4.5; 53 26: 3; 53 27: 2.3; 53 28: 1.8; 53 29: 1.3; 53 30: 0.975; 53 31: 0.8; 53 32: 0.7; 53 33: 0.575; 53 34: 0.425; 53 35: 0.36; 53 36: 0.3; 53 37: 0.24; 53 38: 0.22; 53 39: 0.18; 53 40: 0.15; 53 41: 0.13; 53 42: 0.115; 53 43: 0.1
88 | 1.6 | 53 18: 85; 53 19: 48; 53 20: 30; 53 21: 20; 53 22: 14; 53 23: 10; 53 24: 6.5; 53 25: 5; 53 26: 3.3; 53 27: 2.6; 53 28: 2; 53 29: 1.5; 53 30: 1.1; 53 31: 0.9; 53 32: 0.75; 53 33: 0.65; 53 34: 0.48; 53 35: 0.4; 53 36: 0.34; 53 37: 0.27; 53 38: 0.25; 53 39: 0.2; 53 40: 0.17; 53 41: 0.15; 53 42: 0.125; 53 43: 0.11; 53 44: 0.1
89 | 1.7 | 53 19: 55; 53 20: 33; 53 21: 22; 53 22: 16; 53 23: 11; 53 24: 7.5; 53 25: 5.5; 53 26: 3.8; 53 27: 3; 53 28: 2.2; 53 29: 1.65; 53 30: 1.25; 53 31: 1; 53 32: 0.875; 53 33: 0.725; 53 34: 0.55; 53 35: 0.45; 53 36: 0.38; 53 37: 0.3; 53 38: 0.27; 53 39: 0.22; 53 40: 0.19; 53 41: 0.17; 53 42: 0.145; 53 43: 0.125; 53 44: 0.11
90 | 1.8 | 53 19: 61; 53 20: 38; 53 21: 25; 53 22: 18; 53 23: 12.5; 53 24: 8.5; 53 25: 6.25; 53 26: 4.25; 53 27: 3.4; 53 28: 2.45; 53 29: 1.8; 53 30: 1.4; 53 31: 1.15; 53 32: 1; 53 33: 0.825; 53 34: 0.625; 53 35: 0.5; 53 36: 0.425; 53 37: 0.34; 53 38: 0.3; 53 39: 0.25; 53 40: 0.22; 53 41: 0.19; 53 42: 0.16; 53 43: 0.14; 53 44: 0.125; 53 45: 0.1
91 | 1.9 | 53 19: 70; 53 20: 42.5; 53 21: 28; 53 22: 20; 53 23: 14; 53 24: 9.5; 53 25: 7; 53 26: 4.75; 53 27: 3.7; 53 28: 2.8; 53 29: 2.1; 53 30: 1.55; 53 31: 1.25; 53 32: 1.1; 53 33: 0.9; 53 34: 0.7; 53 35: 0.55; 53 36: 0.475; 53 37: 0.4; 53 38: 0.34; 53 39: 0.28; 53 40: 0.24; 53 41: 0.21; 53 42: 0.18; 53 43: 0.16; 53 44: 0.14; 53 45: 0.11; 53 46: 0.1
92 | 2 | 53 19: 77; 53 20: 45; 53 21: 30; 53 22: 22; 53 23: 15; 53 24: 10; 53 25: 7.5; 53 26: 5.25; 53 27: 4; 53 28: 3; 53 29: 2.3; 53 30: 1.7; 53 31: 1.4; 53 32: 1.2; 53 33: 1; 53 34: 0.75; 53 35: 0.625; 53 36: 0.525; 53 37: 0.44; 53 38: 0.36; 53 39: 0.31; 53 40: 0.27; 53 41: 0.22; 53 42: 0.2; 53 43: 0.17; 53 44: 0.15; 53 45: 0.12; 53 46: 0.11; 53 47: 0.1
93 | 2.1 | 53 20: 50; 53 21: 33; 53 22: 24; 53 23: 16.5; 53 24: 11; 53 25: 8.5; 53 26: 5.75; 53 27: 4.5; 53 28: 3.3; 53 29: 2.6; 53 30: 1.85; 53 31: 1.5; 53 32: 1.35; 53 33: 1.1; 53 34: 0.85; 53 35: 0.675; 53 36: 0.575; 53 37: 0.47; 53 38: 0.4; 53 39: 0.34; 53 40: 0.3; 53 41: 0.24; 53 42: 0.22; 53 43: 0.19; 53 44: 0.165; 53 45: 0.13; 53 46: 0.12; 53 47: 0.11
94 | 2.2 | 53 20: 55; 53 21: 36; 53 22: 26; 53 23: 17; 53 24: 12; 53 25: 9; 53 26: 6.5; 53 27: 5; 53 28: 3.6; 53 29: 2.9; 53 30: 2; 53 31: 1.65; 53 32: 1.5; 53 33: 1.2; 53 34: 0.925; 53 35: 0.75; 53 36: 0.65; 53 37: 0.525; 53 38: 0.44; 53 39: 0.37; 53 40: 0.33; 53 41: 0.27; 53 42: 0.24; 53 43: 0.21; 53 44: 0.185; 53 45: 0.145; 53 46: 0.13; 53 47: 0.12; 53 48: 0.1
95 | 2.3 | 53 20: 60; 53 21: 40; 53 22: 28; 53 23: 18.5; 53 24: 13; 53 25: 10; 53 26: 7; 53 27: 5.4; 53 28: 4; 53 29: 3.1; 53 30: 2.1; 53 31: 1.8; 53 32: 1.6; 53 33: 1.3; 53 34: 1; 53 35: 0.8; 53 36: 0.7; 53 37: 0.575; 53 38: 0.475; 53 39: 0.4; 53 40: 0.36; 53 41: 0.29; 53 42: 0.26; 53 43: 0.23; 53 44: 0.2; 53 45: 0.155; 53 46: 0.14; 53 47: 0.13; 53 48: 0.11
96 | 2.4 | 53 20: 65; 53 21: 42.5; 53 22: 30; 53 23: 20; 53 24: 14; 53 25: 11; 53 26: 7.5; 53 27: 5.75; 53 28: 4.25; 53 29: 3.3; 53 30: 2.2; 53 31: 1.9; 53 32: 1.7; 53 33: 1.4; 53 34: 1.1; 53 35: 0.875; 53 36: 0.75; 53 37: 0.6; 53 38: 0.525; 53 39: 0.44; 53 40: 0.38; 53 41: 0.31; 53 42: 0.28; 53 43: 0.24; 53 44: 0.21; 53 45: 0.17; 53 46: 0.15; 53 47: 0.14; 53 48: 0.12; 53 49: 0.1
97 | 2.5 | 53 20: 70; 53 21: 45; 53 22: 32; 53 23: 22; 53 24: 15; 53 25: 11.5; 53 26: 8; 53 27: 6.25; 53 28: 4.6; 53 29: 3.6; 53 30: 2.6; 53 31: 2.1; 53 32: 1.85; 53 33: 1.5; 53 34: 1.2; 53 35: 0.95; 53 36: 0.8; 53 37: 0.65; 53 38: 0.55; 53 39: 0.47; 53 40: 0.425; 53 41: 0.34; 53 42: 0.3; 53 43: 0.26; 53 44: 0.23; 53 45: 0.185; 53 46: 0.165; 53 47: 0.15; 53 48: 0.13; 53 49: 0.11
98 | 2.6 | 53 20: 75; 53 21: 50; 53 22: 35; 53 23: 24; 53 24: 16; 53 25: 12.5; 53 26: 9; 53 27: 6.75; 53 28: 5; 53 29: 3.9; 53 30: 2.8; 53 31: 2.2; 53 32: 2; 53 33: 1.6; 53 34: 1.3; 53 35: 1; 53 36: 0.9; 53 37: 0.7; 53 38: 0.6; 53 39: 0.5; 53 40: 0.45; 53 41: 0.37; 53 42: 0.32; 53 43: 0.28; 53 44: 0.25; 53 45: 0.2; 53 46: 0.18; 53 47: 0.16; 53 48: 0.14; 53 49: 0.12
99 | 2.7 | 53 20: 80; 53 21: 55; 53 22: 38; 53 23: 25; 53 24: 17; 53 25: 13.5; 53 26: 9.5; 53 27: 7.25; 53 28: 5.25; 53 29: 4.25; 53 30: 3; 53 31: 2.4; 53 32: 2.1; 53 33: 1.7; 53 34: 1.4; 53 35: 1.05; 53 36: 0.95; 53 37: 0.75; 53 38: 0.65; 53 39: 0.55; 53 40: 0.475; 53 41: 0.4; 53 42: 0.35; 53 43: 0.3; 53 44: 0.275; 53 45: 0.21; 53 46: 0.19; 53 47: 0.175; 53 48: 0.15; 53 49: 0.13; 53 50: 0.1
100 | 2.8 | 53 21: 57.5; 53 22: 40; 53 23: 28.5; 53 24: 18.5; 53 25: 14; 53 26: 10.5; 53 27: 7.75; 53 28: 5.75; 53 29: 4.5; 53 30: 3.2; 53 31: 2.6; 53 32: 2.3; 53 33: 1.85; 53 34: 1.5; 53 35: 1.15; 53 36: 1; 53 37: 0.8; 53 38: 0.7; 53 39: 0.6; 53 40: 0.525; 53 41: 0.425; 53 42: 0.37; 53 43: 0.32; 53 44: 0.29; 53 45: 0.23; 53 46: 0.2; 53 47: 0.185; 53 48: 0.16; 53 49: 0.14; 53 50: 0.105
101 | 2.9 | 53 21: 61; 53 22: 44; 53 23: 29; 53 24: 20; 53 25: 15; 53 26: 11; 53 27: 8.5; 53 28: 6.25; 53 29: 4.75; 53 30: 3.4; 53 31: 2.8; 53 32: 2.5; 53 33: 2; 53 34: 1.6; 53 35: 1.25; 53 36: 1.1; 53 37: 0.85; 53 38: 0.75; 53 39: 0.64; 53 40: 0.55; 53 41: 0.45; 53 42: 0.4; 53 43: 0.35; 53 44: 0.31; 53 45: 0.24; 53 46: 0.21; 53 47: 0.2; 53 48: 0.17; 53 49: 0.15; 53 50: 0.11
102 | 3 | 53 21: 65; 53 22: 45; 53 23: 30; 53 24: 21; 53 25: 16; 53 26: 12; 53 27: 9; 53 28: 6.5; 53 29: 5; 53 30: 3.6; 53 31: 3; 53 32: 2.6; 53 33: 2.1; 53 34: 1.7; 53 35: 0.13; 53 36: 1.15; 53 37: 0.9; 53 38: 0.8; 53 39: 0.675; 53 40: 0.6; 53 41: 0.475; 53 42: 0.425; 53 43: 0.37; 53 44: 0.33; 53 45: 0.26; 53 46: 0.23; 53 47: 0.21; 53 48: 0.18; 53 49: 0.155; 53 50: 0.12; 53 51: 0.1
103 | 3.2 | 53 21: 74; 53 22: 52.5; 53 23: 34; 53 24: 24; 53 25: 18; 53 26: 13; 53 27: 10.5; 53 28: 7.5; 53 29: 5.75; 53 30: 4; 53 31: 3.4; 53 32: 3; 53 33: 2.4; 53 34: 1.9; 53 35: 1.5; 53 36: 1.3; 53 37: 1.05; 53 38: 0.9; 53 39: 0.75; 53 40: 0.675; 53 41: 0.55; 53 42: 0.475; 53 43: 0.4; 53 44: 0.37; 53 45: 0.3; 53 46: 0.26; 53 47: 0.24; 53 48: 0.2; 53 49: 0.175; 53 50: 0.135; 53 51: 0.1125
104 | 3.4 | 53 21: 85; 53 22: 60; 53 23: 38; 53 24: 27; 53 25: 20; 53 26: 15; 53 27: 11.5; 53 28: 8.5; 53 29: 6.5; 53 30: 4.5; 53 31: 3.8; 53 32: 3.3; 53 33: 2.7; 53 34: 2.2; 53 35: 1.7; 53 36: 1.5; 53 37: 1.2; 53 38: 1; 53 39: 0.85; 53 40: 0.75; 53 41: 0.6; 53 42: 0.55; 53 43: 0.45; 53 44: 0.425; 53 45: 0.33; 53 46: 0.29; 53 47: 0.27; 53 48: 0.23; 53 49: 0.2; 53 50: 0.15; 53 51: 0.125; 53 52: 0.1
105 | 3.6 | 53 22: 65; 53 23: 44; 53 24: 30; 53 25: 22; 53 26: 16.5; 53 27: 13; 53 28: 9.5; 53 29: 7; 53 30: 5; 53 31: 4.25; 53 32: 3.75; 53 33: 3; 53 34: 2.5; 53 35: 1.9; 53 36: 1.65; 53 37: 1.35; 53 38: 1.15; 53 39: 0.95; 53 40: 0.85; 53 41: 0.675; 53 42: 0.6; 53 43: 0.5; 53 44: 0.475; 53 45: 0.36; 53 46: 0.32; 53 47: 0.3; 53 48: 0.25; 53 49: 0.22; 53 50: 0.17; 53 51: 0.14; 53 52: 0.1075
106 | 3.8 | 53 22: 74; 53 23: 50; 53 24: 34; 53 25: 25; 53 26: 18.5; 53 27: 14; 53 28: 10.5; 53 29: 8; 53 30: 5.5; 53 31: 4.75; 53 32: 4; 53 33: 3.3; 53 34: 2.7; 53 35: 2.1; 53 36: 1.8; 53 37: 1.5; 53 38: 1.275; 53 39: 1.05; 53 40: 0.95; 53 41: 0.75; 53 42: 0.675; 53 43: 0.575; 53 44: 0.525; 53 45: 0.4; 53 46: 0.36; 53 47: 0.34; 53 48: 0.28; 53 49: 0.25; 53 50: 0.185; 53 51: 0.15; 53 52: 0.12; 53 53: 0.1
107 | 4 | 53 22: 80; 53 23: 55; 53 24: 37; 53 25: 27; 53 26: 20; 53 27: 16; 53 28: 11.5; 53 29: 9; 53 30: 6; 53 31: 5; 53 32: 4.5; 53 33: 3.7; 53 34: 3; 53 35: 2.3; 53 36: 2; 53 37: 1.65; 53 38: 0.14; 53 39: 1.2; 53 40: 1; 53 41: 0.8; 53 42: 0.75; 53 43: 0.625; 53 44: 0.575; 53 45: 0.45; 53 46: 0.4; 53 47: 0.36; 53 48: 0.3; 53 49: 0.275; 53 50: 0.21; 53 51: 0.165; 53 52: 0.13; 53 53: 0.11
108 | 4.2 | 53 23: 60; 53 24: 40; 53 25: 30; 53 26: 22; 53 27: 17; 53 28: 12.5; 53 29: 9.5; 53 30: 6.5; 53 31: 5.5; 53 32: 5; 53 33: 4; 53 34: 3.3; 53 35: 2.6; 53 36: 2.2; 53 37: 1.8; 53 38: 1.5; 53 39: 1.3; 53 40: 1.075; 53 41: 0.9; 53 42: 0.8; 53 43: 0.675; 53 44: 0.625; 53 45: 0.5; 53 46: 0.44; 53 47: 0.4; 53 48: 0.33; 53 49: 0.3; 53 50: 0.23; 53 51: 0.18; 53 52: 0.14; 53 53: 0.12
109 | 4.4 | 53 23: 65; 53 24: 44; 53 25: 32; 53 26: 24; 53 27: 19; 53 28: 14; 53 29: 10.5; 53 30: 7.25; 53 31: 6; 53 32: 5.25; 53 33: 4.4; 53 34: 3.6; 53 35: 2.8; 53 36: 2.4; 53 37: 2; 53 38: 1.65; 53 39: 1.4; 53 40: 1.2; 53 41: 1; 53 42: 0.875; 53 43: 0.75; 53 44: 0.7; 53 45: 0.55; 53 46: 0.48; 53 47: 0.44; 53 48: 0.36; 53 49: 0.33; 53 50: 0.25; 53 51: 0.2; 53 52: 0.155; 53 53: 0.13; 53 54: 0.1
110 | 4.6 | 53 23: 70; 53 24: 48; 53 25: 35; 53 26: 26; 53 27: 20.5; 53 28: 15; 53 29: 11.5; 53 30: 7.75; 53 31: 6.5; 53 32: 6; 53 33: 4.75; 53 34: 4; 53 35: 3; 53 36: 2.6; 53 37: 2.175; 53 38: 1.8; 53 39: 1.5; 53 40: 1.3; 53 41: 1.1; 53 42: 0.95; 53 43: 0.8; 53 44: 0.75; 53 45: 0.6; 53 46: 0.525; 53 47: 0.475; 53 48: 0.38; 53 49: 0.36; 53 50: 0.27; 53 51: 0.21; 53 52: 0.17; 53 53: 0.14; 53 54: 0.11
111 | 4.8 | 53 23: 75; 53 24: 52.5; 53 25: 38; 53 26: 28; 53 27: 23; 53 28: 16.5; 53 29: 12.5; 53 30: 8.5; 53 31: 7; 53 32: 6.5; 53 33: 5.25; 53 34: 4.25; 53 35: 3.2; 53 36: 2.8; 53 37: 2.4; 53 38: 2; 53 39: 1.6; 53 40: 1.4; 53 41: 1.2; 53 42: 1.05; 53 43: 0.875; 53 44: 0.8; 53 45: 0.65; 53 46: 0.575; 53 47: 0.5; 53 48: 0.4; 53 49: 0.38; 53 50: 0.3; 53 51: 0.23; 53 52: 0.185; 53 53: 0.15; 53 54: 0.12; 53 55: 0.1
112 | 5 | 53 23: 80; 53 24: 55; 53 25: 40; 53 26: 30; 53 27: 24; 53 28: 18; 53 29: 13.5; 53 30: 9.25; 53 31: 7.5; 53 32: 7; 53 33: 5.5; 53 34: 4.5; 53 35: 3.6; 53 36: 3; 53 37: 2.6; 53 38: 2.2; 53 39: 1.7; 53 40: 1.5; 53 41: 1.3; 53 42: 1.1; 53 43: 0.95; 53 44: 0.85; 53 45: 0.7; 53 46: 0.6; 53 47: 0.54; 53 48: 0.45; 53 49: 0.4; 53 50: 0.32; 53 51: 0.25; 53 52: 0.2; 53 53: 0.165; 53 54: 0.13; 53 55: 0.11
113 | 5.2 | 53 24: 60; 53 25: 43; 53 26: 32; 53 27: 26; 53 28: 19; 53 29: 15; 53 30: 10; 53 31: 8.25; 53 32: 7.5; 53 33: 6; 53 34: 4.75; 53 35: 3.8; 53 36: 3.2; 53 37: 2.8; 53 38: 2.4; 53 39: 1.9; 53 40: 1.65; 53 41: 1.4; 53 42: 1.2; 53 43: 1.05; 53 44: 0.95; 53 45: 0.75; 53 46: 0.65; 53 47: 0.58; 53 48: 0.5; 53 49: 0.45; 53 50: 0.35; 53 51: 0.275; 53 52: 0.21; 53 53: 0.175; 53 54: 0.14; 53 55: 0.12
114 | 5.4 | 53 24: 66; 53 25: 47; 53 26: 35; 53 27: 28; 53 28: 21; 53 29: 16.5; 53 30: 11; 53 31: 9; 53 32: 8; 53 33: 6.5; 53 34: 5.25; 53 35: 4.25; 53 36: 3.5; 53 37: 3; 53 38: 2.6; 53 39: 2.1; 53 40: 1.8; 53 41: 1.5; 53 42: 1.3; 53 43: 1.1; 53 44: 1; 53 45: 0.825; 53 46: 0.7; 53 47: 0.625; 53 48: 0.55; 53 49: 0.475; 53 50: 0.38; 53 51: 0.295; 53 52: 0.24; 53 53: 0.19; 53 54: 0.15; 53 55: 0.13; 53 56: 0.1
115 | 5.6 | 53 24: 70; 53 25: 50; 53 26: 38; 53 27: 30; 53 28: 22; 53 29: 17.5; 53 30: 12; 53 31: 9.5; 53 32: 8.75; 53 33: 7; 53 34: 5.75; 53 35: 4.5; 53 36: 3.8; 53 37: 3.2; 53 38: 2.7; 53 39: 2.2; 53 40: 1.9; 53 41: 1.6; 53 42: 1.4; 53 43: 1.2; 53 44: 1.05; 53 45: 0.9; 53 46: 0.75; 53 47: 0.675; 53 48: 0.6; 53 49: 0.525; 53 50: 0.4; 53 51: 0.31; 53 52: 0.25; 53 53: 0.2; 53 54: 0.16; 53 55: 0.135; 53 56: 0.11
116 | 5.8 | 53 24: 75; 53 25: 55; 53 26: 40; 53 27: 32; 53 28: 24; 53 29: 19; 53 30: 13; 53 31: 10.25; 53 32: 9.5; 53 33: 7.5; 53 34: 6; 53 35: 4.75; 53 36: 4; 53 37: 3.4; 53 38: 2.9; 53 39: 2.4; 53 40: 2; 53 41: 1.7; 53 42: 1.5; 53 43: 1.3; 53 44: 1.15; 53 45: 0.95; 53 46: 0.8; 53 47: 0.725; 53 48: 0.65; 53 49: 0.55; 53 50: 0.425; 53 51: 0.34; 53 52: 0.27; 53 53: 0.22; 53 54: 0.17; 53 55: 0.145; 53 56: 0.115; 53 57: 0.1
117 | 6 | 53 24: 80; 53 25: 60; 53 26: 42.5; 53 27: 34; 53 28: 25; 53 29: 20; 53 30: 14; 53 31: 11; 53 32: 10; 53 33: 8; 53 34: 6.5; 53 35: 5; 53 36: 4.25; 53 37: 3.6; 53 38: 3.1; 53 39: 2.6; 53 40: 2.2; 53 41: 1.8; 53 42: 1.6; 53 43: 1.4; 53 44: 1.25; 53 45: 1; 53 46: 0.85; 53 47: 0.75; 53 48: 0.7; 53 49: 0.6; 53 50: 0.45; 53 51: 0.35; 53 52: 0.28; 53 53: 0.23; 53 54: 0.18; 53 55: 0.15; 53 56: 0.12; 53 57: 0.105
118 | 6.5 | 53 25: 70; 53 26: 50; 53 27: 40; 53 28: 30; 53 29: 23; 53 30: 16.5; 53 31: 12.5; 53 32: 11.75; 53 33: 9.5; 53 34: 7.5; 53 35: 6; 53 36: 5; 53 37: 4.25; 53 38: 3.6; 53 39: 3; 53 40: 2.6; 53 41: 2.1; 53 42: 1.9; 53 43: 1.6; 53 44: 1.5; 53 45: 1.2; 53 46: 1; 53 47: 0.9; 53 48: 0.8; 53 49: 0.7; 53 50: 0.525; 53 51: 0.41; 53 52: 0.33; 53 53: 0.265; 53 54: 0.21; 53 55: 0.155; 53 56: 0.145; 53 57: 0.12; 53 58: 0.1
119 | 7 | 53 25: 80; 53 26: 59; 53 27: 46; 53 28: 34; 53 29: 27; 53 30: 18.5; 53 31: 15; 53 32: 13.5; 53 33: 11; 53 34: 8.5; 53 35: 7; 53 36: 5.75; 53 37: 5; 53 38: 4.25; 53 39: 3.4; 53 40: 3; 53 41: 2.5; 53 42: 2.2; 53 43: 1.85; 53 44: 1.7; 53 45: 1.4; 53 46: 1.15; 53 47: 1; 53 48: 0.95; 53 49: 0.8; 53 50: 0.6; 53 51: 0.475; 53 52: 0.38; 53 53: 0.31; 53 54: 0.24; 53 55: 0.2; 53 56: 0.17; 53 57: 0.15; 53 58: 0.115; 53 59: 0.1
120 | 7.5 | 53 26: 67; 53 27: 52.5; 53 28: 39; 53 29: 30; 53 30: 22; 53 31: 17; 53 32: 15; 53 33: 12.5; 53 34: 10; 53 35: 8; 53 36: 6.5; 53 37: 5.75; 53 38: 4.5; 53 39: 3.9; 53 40: 3.4; 53 41: 2.8; 53 42: 2.5; 53 43: 2.1; 53 44: 1.9; 53 45: 1.55; 53 46: 1.3; 53 47: 1.15; 53 48: 1.05; 53 49: 0.9; 53 50: 0.7; 53 51: 0.54; 53 52: 0.45; 53 53: 0.36; 53 54: 0.28; 53 55: 0.23; 53 56: 0.19; 53 57: 0.16; 53 58: 0.13; 53 59: 0.115; 53 60: 0.1
121 | 8 | 53 26: 75; 53 27: 60; 53 28: 45; 53 29: 33; 53 30: 24; 53 31: 19; 53 32: 17.5; 53 33: 14; 53 34: 11; 53 35: 9; 53 36: 7.5; 53 37: 6.5; 53 38: 5; 53 39: 4.5; 53 40: 3.8; 53 41: 3.2; 53 42: 2.8; 53 43: 2.4; 53 44: 2.2; 53 45: 1.8; 53 46: 1.5; 53 47: 1.3; 53 48: 1.2; 53 49: 1.05; 53 50: 0.8; 53 51: 0.61; 53 52: 0.5; 53 53: 0.4; 53 54: 0.31; 53 55: 0.26; 53 56: 0.22; 53 57: 0.18; 53 58: 0.15; 53 59: 0.13; 53 60: 0.11
122 | 8.5 | 53 27: 67; 53 28: 50; 53 29: 38; 53 30: 28; 53 31: 22; 53 32: 20; 53 33: 15.75; 53 34: 12.25; 53 35: 10; 53 36: 8.5; 53 37: 7; 53 38: 5.5; 53 39: 5; 53 40: 4.25; 53 41: 3.7; 53 42: 3.2; 53 43: 2.7; 53 44: 2.5; 53 45: 2; 53 46: 1.65; 53 47: 1.5; 53 48: 1.35; 53 49: 1.2; 53 50: 0.9; 53 51: 0.7; 53 52: 0.575; 53 53: 0.45; 53 54: 0.35; 53 55: 0.29; 53 56: 0.25; 53 57: 0.2; 53 58: 0.17; 53 59: 0.145; 53 60: 0.125; 53 61: 0.1
123 | 9 | 53 27: 75; 53 28: 55; 53 29: 42.5; 53 30: 31; 53 31: 24; 53 32: 22; 53 33: 18; 53 34: 14; 53 35: 11.5; 53 36: 9.5; 53 37: 8; 53 38: 6.25; 53 39: 5.5; 53 40: 4.75; 53 41: 4; 53 42: 3.5; 53 43: 3; 53 44: 2.8; 53 45: 2.2; 53 46: 1.9; 53 47: 1.65; 53 48: 1.5; 53 49: 1.3; 53 50: 1; 53 51: 0.75; 53 52: 0.65; 53 53: 0.5; 53 54: 0.4; 53 55: 0.32; 53 56: 0.28; 53 57: 0.22; 53 58: 0.19; 53 59: 0.16; 53 60: 0.14; 53 61: 0.11; 53 62: 0.1
124 | 9.5 | 53 27: 80; 53 28: 62.5; 53 29: 47.5; 53 30: 34; 53 31: 27; 53 32: 25; 53 33: 20; 53 34: 15; 53 35: 12.5; 53 36: 10.5; 53 37: 9; 53 38: 7; 53 39: 6.2; 53 40: 5.25; 53 41: 4.4; 53 42: 4; 53 43: 3.4; 53 44: 3; 53 45: 2.5; 53 46: 2.1; 53 47: 1.8; 53 48: 1.65; 53 49: 1.475; 53 50: 1.1; 53 51: 0.85; 53 52: 0.7; 53 53: 0.55; 53 54: 0.45; 53 55: 0.36; 53 56: 0.31; 53 57: 0.25; 53 58: 0.21; 53 59: 0.18; 53 60: 0.15; 53 61: 0.125; 53 62: 0.11
125 | 10 | 53 28: 70; 53 29: 51; 53 30: 38; 53 31: 30; 53 32: 27; 53 33: 22; 53 34: 17; 53 35: 14; 53 36: 11.5; 53 37: 10; 53 38: 7.5; 53 39: 6.8; 53 40: 6; 53 41: 4.9; 53 42: 4.4; 53 43: 3.7; 53 44: 3.3; 53 45: 2.7; 53 46: 2.3; 53 47: 2; 53 48: 1.85; 53 49: 1.6; 53 50: 1.2; 53 51: 0.925; 53 52: 0.775; 53 53: 0.6; 53 54: 0.5; 53 55: 0.4; 53 56: 0.34; 53 57: 0.28; 53 58: 0.23; 53 59: 0.2; 53 60: 0.17; 53 61: 0.14; 53 62: 0.12; 53 63: 0.1
126 | 11 | 53 28: 80; 53 29: 60; 53 30: 45; 53 31: 35; 53 32: 32; 53 33: 26; 53 34: 20; 53 35: 17; 53 36: 14; 53 37: 12; 53 38: 9; 53 39: 8; 53 40: 7; 53 41: 6; 53 42: 5.25; 53 43: 4.5; 53 44: 4; 53 45: 3.2; 53 46: 2.8; 53 47: 2.4; 53 48: 2.2; 53 49: 1.95; 53 50: 1.5; 53 51: 1.1; 53 52: 0.95; 53 53: 0.75; 53 54: 0.6; 53 55: 0.475; 53 56: 0.4; 53 57: 0.34; 53 58: 0.28; 53 59: 0.24; 53 60: 0.2; 53 61: 0.165; 53 62: 0.15; 53 63: 0.12; 53 64: 0.11; 53 65: 0.1
127 | 12 | 53 29: 70; 53 30: 54; 53 31: 42.5; 53 32: 38; 53 33: 31; 53 34: 24; 53 35: 20; 53 36: 16.5; 53 37: 14; 53 38: 10.5; 53 39: 9.5; 53 40: 8.5; 53 41: 7; 53 42: 6.25; 53 43: 5.25; 53 44: 4.75; 53 45: 3.8; 53 46: 3.2; 53 47: 2.8; 53 48: 2.6; 53 49: 2.3; 53 50: 1.75; 53 51: 1.3; 53 52: 1.1; 53 53: 0.875; 53 54: 0.7; 53 55: 0.575; 53 56: 0.475; 53 57: 0.4; 53 58: 0.32; 53 59: 0.28; 53 60: 0.24; 53 61: 0.2; 53 62: 0.175; 53 63: 0.14; 53 64: 0.13; 53 65: 0.115; 53 66: 0.1
128 | 13 | 53 29: 80; 53 30: 62.5; 53 31: 50; 53 32: 45; 53 33: 36; 53 34: 28; 53 35: 23; 53 36: 19; 53 37: 16; 53 38: 12.5; 53 39: 11; 53 40: 10; 53 41: 8; 53 42: 7.25; 53 43: 6; 53 44: 5.5; 53 45: 4.5; 53 46: 3.8; 53 47: 3.2; 53 48: 3; 53 49: 2.6; 53 50: 2; 53 51: 1.5; 53 52: 1.3; 53 53: 1; 53 54: 0.8; 53 55: 0.65; 53 56: 0.55; 53 57: 0.46; 53 58: 0.37; 53 59: 0.32; 53 60: 0.28; 53 61: 0.23; 53 62: 0.2; 53 63: 0.16; 53 64: 0.15; 53 65: 0.135; 53 66: 0.115; 53 67: 0.1
129 | 14 | 53 30: 72.5; 53 31: 57.5; 53 32: 52.5; 53 33: 42.5; 53 34: 32; 53 35: 27; 53 36: 22; 53 37: 19; 53 38: 14.5; 53 39: 12.5; 53 40: 11.5; 53 41: 9.5; 53 42: 8.5; 53 43: 7; 53 44: 6.5; 53 45: 5; 53 46: 4.5; 53 47: 3.8; 53 48: 3.5; 53 49: 3.1; 53 50: 2.3; 53 51: 1.75; 53 52: 1.5; 53 53: 1.15; 53 54: 0.925; 53 55: 0.75; 53 56: 0.65; 53 57: 0.525; 53 58: 0.44; 53 59: 0.38; 53 60: 0.32; 53 61: 0.26; 53 62: 0.24; 53 63: 0.19; 53 64: 0.175; 53 65: 0.15; 53 66: 0.135; 53 67: 0.115; 53 68: 0.1
130 | 15 | 53 30: 80; 53 31: 65; 53 32: 60; 53 33: 47.5; 53 34: 37; 53 35: 30; 53 36: 25; 53 37: 22; 53 38: 16.5; 53 39: 14; 53 40: 13; 53 41: 10.075; 53 42: 9.5; 53 43: 8; 53 44: 7; 53 45: 5.75; 53 46: 5; 53 47: 4.4; 53 48: 4; 53 49: 3.5; 53 50: 2.6; 53 51: 2; 53 52: 1.7; 53 53: 1.3; 53 54: 1.05; 53 55: 0.85; 53 56: 0.75; 53 57: 0.6; 53 58: 0.5; 53 59: 0.425; 53 60: 0.36; 53 61: 0.3; 53 62: 0.27; 53 63: 0.22; 53 64: 0.2; 53 65: 0.17; 53 66: 0.15; 53 67: 0.13; 53 68: 0.115; 53 69: 0.1
131 | 16 | 53 31: 75; 53 32: 67.5; 53 33: 55; 53 34: 40; 53 35: 34; 53 36: 28; 53 37: 24; 53 38: 18.5; 53 39: 16.5; 53 40: 15; 53 41: 12; 53 42: 11; 53 43: 9; 53 44: 8; 53 45: 6.5; 53 46: 5.75; 53 47: 5; 53 48: 4.5; 53 49: 4; 53 50: 3; 53 51: 2.2; 53 52: 1.9; 53 53: 1.5; 53 54: 1.2; 53 55: 0.95; 53 56: 0.85; 53 57: 0.7; 53 58: 0.55; 53 59: 0.475; 53 60: 0.4; 53 61: 0.34; 53 62: 0.3; 53 63: 0.25; 53 64: 0.22; 53 65: 0.19; 53 66: 0.17; 53 67: 0.15; 53 68: 0.13; 53 69: 0.11; 53 70: 0.1
132 | 17 | 53 31: 80; 53 32: 75; 53 33: 62.5; 53 34: 47; 53 35: 38; 53 36: 32; 53 37: 27; 53 38: 21; 53 39: 18.5; 53 40: 17; 53 41: 14; 53 42: 12.5; 53 43: 10.5; 53 44: 9; 53 45: 7.25; 53 46: 6.5; 53 47: 5.75; 53 48: 5; 53 49: 4.5; 53 50: 3.4; 53 51: 2.5; 53 52: 2.2; 53 53: 1.7; 53 54: 1.35; 53 55: 1.1; 53 56: 0.95; 53 57: 0.775; 53 58: 0.625; 53 59: 0.55; 53 60: 0.45; 53 61: 0.38; 53 62: 0.34; 53 63: 0.28; 53 64: 0.26; 53 65: 0.22; 53 66: 0.19; 53 67: 0.17; 53 68: 0.15; 53 69: 0.125; 53 70: 0.115; 53 71: 0.1
133 | 18 | 53 33: 70; 53 34: 52; 53 35: 42.5; 53 36: 36; 53 37: 30; 53 38: 24; 53 39: 20.5; 53 40: 19; 53 41: 15; 53 42: 14; 53 43: 12; 53 44: 10; 53 45: 8; 53 46: 7; 53 47: 6.25; 53 48: 5.5; 53 49: 5; 53 50: 3.8; 53 51: 2.9; 53 52: 2.4; 53 53: 1.9; 53 54: 1.5; 53 55: 1.25; 53 56: 1.05; 53 57: 0.85; 53 58: 0.7; 53 59: 0.6; 53 60: 0.5; 53 61: 0.425; 53 62: 0.38; 53 63: 0.32; 53 64: 28; 53 65: 0.24; 53 66: 0.21; 53 67: 0.185; 53 68: 0.17; 53 69: 0.14; 53 70: 0.1275; 53 71: 0.11; 53 72: 0.1
134 | 19 | 53 33: 77.5; 53 34: 57; 53 35: 47.5; 53 36: 40; 53 37: 33; 53 38: 26; 53 39: 23; 53 40: 21; 53 41: 17; 53 42: 15.5; 53 43: 13; 53 44: 11; 53 45: 9; 53 46: 8; 53 47: 7; 53 48: 6.25; 53 49: 5.5; 53 50: 4.25; 53 51: 3.1; 53 52: 2.8; 53 53: 2.1; 53 54: 1.7; 53 55: 1.35; 53 56: 1.15; 53 57: 0.95; 53 58: 0.75; 53 59: 0.675; 53 60: 0.55; 53 61: 0.475; 53 62: 0.425; 53 63: 0.35; 53 64: 0.31; 53 65: 0.27; 53 66: 0.24; 53 67: 0.21; 53 68: 0.185; 53 69: 0.155; 53 70: 0.14; 53 71: 0.12; 53 72: 0.11; 53 73: 0.1
135 | 20 | 53 34: 63; 53 35: 54; 53 36: 44; 53 37: 36; 53 38: 28; 53 39: 26; 53 40: 24; 53 41: 18.5; 53 42: 17; 53 43: 15; 53 44: 12; 53 45: 10; 53 46: 9; 53 47: 7.75; 53 48: 7; 53 49: 6; 53 50: 4.6; 53 51: 3.3; 53 52: 3; 53 53: 2.3; 53 54: 1.85; 53 55: 1.5; 53 56: 1.3; 53 57: 1.05; 53 58: 0.85; 53 59: 0.75; 53 60: 0.65; 53 61: 0.525; 53 62: 0.475; 53 63: 0.38; 53 64: 0.35; 53 65: 0.3; 53 66: 0.26; 53 67: 0.23; 53 68: 0.2; 53 69: 0.17; 53 70: 0.155; 53 71: 0.135; 53 72: 0.12; 53 73: 0.11; 53 74: 0.1
136 | 21 | 53 34: 70; 53 35: 60; 53 36: 48; 53 37: 40; 53 38: 31; 53 39: 28; 53 40: 27; 53 41: 20; 53 42: 19; 53 43: 16.5; 53 44: 13.5; 53 45: 11; 53 46: 10; 53 47: 8.5; 53 48: 7.5; 53 49: 6.75; 53 50: 5; 53 51: 3.8; 53 52: 3.3; 53 53: 2.6; 53 54: 2; 53 55: 1.65; 53 56: 1.4; 53 57: 1.15; 53 58: 0.925; 53 59: 0.8; 53 60: 0.725; 53 61: 0.575; 53 62: 0.5; 53 63: 0.425; 53 64: 0.38; 53 65: 0.32; 53 66: 0.28; 53 67: 0.26; 53 68: 0.22; 53 69: 0.19; 53 70: 0.17; 53 71: 0.15; 53 72: 0.135; 53 73: 0.12; 53 74: 0.1
137 | 22 | 53 34: 75; 53 35: 65; 53 36: 54; 53 37: 45; 53 38: 34; 53 39: 30; 53 40: 30; 53 41: 22; 53 42: 21; 53 43: 18; 53 44: 15; 53 45: 12; 53 46: 11; 53 47: 9.5; 53 48: 8.5; 53 49: 7.5; 53 50: 5.5; 53 51: 4; 53 52: 3.6; 53 53: 2.8; 53 54: 2.2; 53 55: 1.8; 53 56: 1.55; 53 57: 1.3; 53 58: 1; 53 59: 0.9; 53 60: 0.8; 53 61: 0.625; 53 62: 0.55; 53 63: 0.475; 53 64: 0.425; 53 65: 0.35; 53 66: 0.31; 53 67: 0.28; 53 68: 0.24; 53 69: 0.21; 53 70: 0.185; 53 71: 0.16; 53 72: 0.145; 53 73: 0.13; 53 74: 0.12; 53 75: 0.1
138 | 23 | 53 34: 80; 53 35: 70; 53 36: 58; 53 37: 50; 53 38: 37; 53 39: 33; 53 40: 32; 53 41: 25; 53 42: 23; 53 43: 20; 53 44: 16; 53 45: 13; 53 46: 12; 53 47: 10; 53 48: 9; 53 49: 8.25; 53 50: 6; 53 51: 4.25; 53 52: 4; 53 53: 3; 53 54: 2.4; 53 55: 2; 53 56: 1.65; 53 57: 1.4; 53 58: 1.1; 53 59: 1; 53 60: 0.85; 53 61: 0.7; 53 62: 0.6; 53 63: 0.5; 53 64: 0.45; 53 65: 0.38; 53 66: 0.34; 53 67: 0.3; 53 68: 0.26; 53 69: 0.23; 53 70: 0.2; 53 71: 0.175; 53 72: 0.1575; 53 73: 0.14; 53 74: 0.13; 53 75: 0.11
139 | 24 | 53 35: 76; 53 36: 64; 53 37: 55; 53 38: 40; 53 39: 35; 53 40: 34; 53 41: 27; 53 42: 24; 53 43: 21; 53 44: 18; 53 45: 14; 53 46: 13; 53 47: 11; 53 48: 10; 53 49: 9; 53 50: 6.5; 53 51: 4.6; 53 52: 4.25; 53 53: 3.3; 53 54: 2.6; 53 55: 2.1; 53 56: 1.8; 53 57: 1.5; 53 58: 1.2; 53 59: 1.05; 53 60: 0.925; 53 61: 0.75; 53 62: 0.65; 53 63: 0.55; 53 64: 0.475; 53 65: 0.4; 53 66: 0.37; 53 67: 0.33; 53 68: 0.28; 53 69: 0.24; 53 70: 0.22; 53 71: 0.19; 53 72: 0.17; 53 73: 0.15; 53 74: 0.14; 53 75: 0.12
140 | 25 | 53 35: 80; 53 36: 68; 53 37: 60; 53 38: 43; 53 39: 38; 53 40: 38; 53 41: 28; 53 42: 26; 53 43: 23; 53 44: 19; 53 45: 15; 53 46: 14; 53 47: 12; 53 48: 10.5; 53 49: 9.5; 53 50: 7; 53 51: 5; 53 52: 4.5; 53 53: 3.5; 53 54: 2.8; 53 55: 2.3; 53 56: 1.95; 53 57: 1.6; 53 58: 1.3; 53 59: 1.15; 53 60: 1; 53 61: 0.8; 53 62: 0.7; 53 63: 0.6; 53 64: 0.525; 53 65: 0.425; 53 66: 0.4; 53 67: 0.35; 53 68: 0.3; 53 69: 0.26; 53 70: 0.24; 53 71: 0.2; 53 72: 0.18; 53 73: 0.165; 53 74: 0.15; 53 75: 0.13
141 | 26 | 53 36: 73; 53 37: 62.5; 53 38: 47; 53 39: 42; 53 40: 40; 53 41: 31; 53 42: 28; 53 43: 25; 53 44: 20; 53 45: 16.5; 53 46: 15; 53 47: 13; 53 48: 11.5; 53 49: 10.25; 53 50: 7.5; 53 51: 5.4; 53 52: 5; 53 53: 3.8; 53 54: 3; 53 55: 2.5; 53 56: 2.1; 53 57: 1.75; 53 58: 1.5; 53 59: 1.2; 53 60: 1.05; 53 61: 0.875; 53 62: 0.75; 53 63: 0.65; 53 64: 0.575; 53 65: 0.475; 53 66: 0.425; 53 67: 0.38; 53 68: 0.33; 53 69: 0.28; 53 70: 0.26; 53 71: 0.2175; 53 72: 0.2; 53 73: 0.18; 53 74: 0.16; 53 75: 0.14
142 | 27 | 53 36: 78; 53 37: 68; 53 38: 50; 53 39: 45; 53 40: 42.5; 53 41: 33; 53 42: 30; 53 43: 26; 53 44: 22; 53 45: 18; 53 46: 16; 53 47: 14; 53 48: 12; 53 49: 11; 53 50: 8; 53 51: 5.75; 53 52: 5.25; 53 53: 4.25; 53 54: 3.2; 53 55: 2.7; 53 56: 2.3; 53 57: 1.9; 53 58: 1.6; 53 59: 1.3; 53 60: 1.15; 53 61: 0.95; 53 62: 0.8; 53 63: 0.7; 53 64: 0.6; 53 65: 0.5; 53 66: 0.475; 53 67: 0.4; 53 68: 0.35; 53 69: 0.3; 53 70: 0.285; 53 71: 0.23; 53 72: 0.21; 53 73: 0.19; 53 74: 0.17; 53 75: 0.15
143 | 28 | 53 37: 72.5; 53 38: 53; 53 39: 48; 53 40: 47.5; 53 41: 36; 53 42: 32; 53 43: 28; 53 44: 24; 53 45: 18; 53 46: 17; 53 47: 15; 53 48: 13; 53 49: 12; 53 50: 8.5; 53 51: 6.25; 53 52: 5.75; 53 53: 4.5; 53 54: 3.4; 53 55: 2.9; 53 56: 2.4; 53 57: 2; 53 58: 1.7; 53 59: 1.4; 53 60: 1.25; 53 61: 1; 53 62: 0.85; 53 63: 0.75; 53 64: 0.65; 53 65: 0.525; 53 66: 0.5; 53 67: 0.45; 53 68: 0.38; 53 69: 0.32; 53 70: 0.295; 53 71: 0.24; 53 72: 0.23; 53 73: 0.2; 53 74: 0.185; 53 75: 0.16
144 | 29 | 53 37: 80; 53 38: 60; 53 39: 51; 53 40: 50; 53 41: 38; 53 42: 34; 53 43: 30; 53 44: 25; 53 45: 20; 53 46: 19; 53 47: 16; 53 48: 14; 53 49: 13; 53 50: 9; 53 51: 6.5; 53 52: 6; 53 53: 4.75; 53 54: 3.7; 53 55: 3; 53 56: 2.6; 53 57: 2.1; 53 58: 1.8; 53 59: 1.5; 53 60: 1.3; 53 61: 1.05; 53 62: 0.9; 53 63: 0.8; 53 64: 0.7; 53 65: 0.55; 53 66: 0.525; 53 67: 0.475; 53 68: 0.4; 53 69: 0.34; 53 70: 0.31; 53 71: 0.26; 53 72: 0.24; 53 73: 0.2175; 53 74: 0.2; 53 75: 0.17
145 | 30 | 53 38: 62.5; 53 39: 55; 53 40: 55; 53 41: 40; 53 42: 37; 53 43: 32; 53 44: 27; 53 45: 22; 53 46: 20; 53 47: 17; 53 48: 15; 53 49: 14; 53 50: 10; 53 51: 7; 53 52: 6.5; 53 53: 5; 53 54: 4; 53 55: 3.2; 53 56: 2.8; 53 57: 2.15; 53 58: 1.9; 53 59: 1.6; 53 60: 1.5; 53 61: 1.15; 53 62: 1; 53 63: 0.85; 53 64: 0.75; 53 65: 0.6; 53 66: 0.575; 53 67: 0.5; 53 68: 0.44; 53 69: 0.37; 53 70: 0.34; 53 71: 0.28; 53 72: 0.26; 53 73: 0.23; 53 74: 0.21; 53 75: 0.18
146 | 32 | 53 38: 70; 53 39: 63; 53 40: 60; 53 41: 45; 53 42: 42.5; 53 43: 36; 53 44: 30; 53 45: 25; 53 46: 22; 53 47: 19.5; 53 48: 17; 53 49: 15; 53 50: 11.25; 53 51: 8; 53 52: 7.5; 53 53: 5.75; 53 54: 4.5; 53 55: 3.6; 53 56: 3.1; 53 57: 2.6; 53 58: 2.2; 53 59: 1.8; 53 60: 1.7; 53 61: 1.3; 53 62: 1.1; 53 63: 0.95; 53 64: 0.85; 53 65: 0.675; 53 66: 0.65; 53 67: 0.575; 53 68: 0.5; 53 69: 0.41; 53 70: 0.38; 53 71: 0.31; 53 72: 0.295; 53 73: 0.26; 53 74: 0.24; 53 75: 0.2025
147 | 34 | 53 38: 80; 53 39: 70; 53 40: 70; 53 41: 52.5; 53 42: 47.5; 53 43: 40; 53 44: 34; 53 45: 28; 53 46: 26; 53 47: 22; 53 48: 19; 53 49: 17; 53 50: 12.5; 53 51: 9; 53 52: 8.5; 53 53: 6.5; 53 54: 5; 53 55: 4; 53 56: 3.5; 53 57: 3; 53 58: 2.5; 53 59: 2; 53 60: 1.85; 53 61: 1.5; 53 62: 1.25; 53 63: 1.075; 53 64: 0.95; 53 65: 0.75; 53 66: 0.725; 53 67: 0.65; 53 68: 0.55; 53 69: 0.475; 53 70: 0.425; 53 71: 0.35; 53 72: 0.33; 53 73: 0.3; 53 74: 0.27; 53 75: 0.225
148 | 36 | 53 39: 78; 53 40: 75; 53 41: 57.5; 53 42: 52.5; 53 43: 45; 53 44: 38; 53 45: 30; 53 46: 28; 53 47: 24; 53 48: 21; 53 49: 19; 53 50: 14; 53 51: 10; 53 52: 9.25; 53 53: 7; 53 54: 5.75; 53 55: 4.5; 53 56: 4; 53 57: 3.3; 53 58: 2.8; 53 59: 2.2; 53 60: 2; 53 61: 1.65; 53 62: 1.4; 53 63: 1.2; 53 64: 1.05; 53 65: 0.85; 53 66: 0.8; 53 67: 0.7; 53 68: 0.625; 53 69: 0.525; 53 70: 0.475; 53 71: 0.4; 53 72: 0.36; 53 73: 0.34; 53 74: 0.3; 53 75: 0.26
149 | 38 | 53 41: 65; 53 42: 60; 53 43: 50; 53 44: 42.5; 53 45: 34; 53 46: 32; 53 47: 27; 53 48: 23; 53 49: 22; 53 50: 16; 53 51: 11; 53 52: 10.25; 53 53: 8; 53 54: 6.25; 53 55: 5; 53 56: 4.5; 53 57: 3.7; 53 58: 3; 53 59: 2.5; 53 60: 2.2; 53 61: 1.8; 53 62: 1.55; 53 63: 1.35; 53 64: 1.2; 53 65: 0.95; 53 66: 0.9; 53 67: 0.8; 53 68: 0.7; 53 69: 0.6; 53 70: 0.525; 53 71: 0.45; 53 72: 0.4; 53 73: 0.37; 53 74: 0.34; 53 75: 0.29
150 | 40 | 53 41: 70; 53 42: 65; 53 43: 55; 53 44: 45; 53 45: 37; 53 46: 34; 53 47: 30; 53 48: 26; 53 49: 24; 53 50: 17; 53 51: 12; 53 52: 11.5; 53 53: 8.75; 53 54: 7; 53 55: 5.5; 53 56: 5; 53 57: 4; 53 58: 3.3; 53 59: 2.7; 53 60: 2.4; 53 61: 2; 53 62: 1.7; 53 63: 1.5; 53 64: 1.3; 53 65: 1.05; 53 66: 1; 53 67: 0.875; 53 68: 0.75; 53 69: 0.65; 53 70: 0.575; 53 71: 0.475; 53 72: 0.45; 53 73: 0.4; 53 74: 0.37; 53 75: 0.32
151 | 42 | 53 41: 75; 53 42: 70; 53 43: 60; 53 44: 50; 53 45: 40; 53 46: 38; 53 47: 32; 53 48: 28; 53 49: 26; 53 50: 18.5; 53 51: 13; 53 52: 12.5; 53 53: 9.5; 53 54: 7.5; 53 55: 6; 53 56: 5.25; 53 57: 4.25; 53 58: 3.7; 53 59: 3; 53 60: 2.7; 53 61: 2.2; 53 62: 1.9; 53 63: 1.65; 53 64: 1.4; 53 65: 1.15; 53 66: 1.1; 53 67: 0.95; 53 68: 0.825; 53 69: 0.7; 53 70: 0.65; 53 71: 0.525; 53 72: 0.5; 53 73: 0.45; 53 74: 0.4; 53 75: 0.35
152 | 44 | 53 41: 80; 53 42: 75; 53 43: 67.5; 53 44: 55; 53 45: 44; 53 46: 40; 53 47: 35; 53 48: 30; 53 49: 28; 53 50: 20; 53 51: 14; 53 52: 13.5; 53 53: 10.5; 53 54: 8.25; 53 55: 6.5; 53 56: 5.75; 53 57: 4.75; 53 58: 4; 53 59: 3.2; 53 60: 2.9; 53 61: 2.4; 53 62: 2; 53 63: 1.8; 53 64: 1.6; 53 65: 1.25; 53 66: 1.2; 53 67: 1.05; 53 68: 0.9; 53 69: 0.775; 53 70: 0.7; 53 71: 0.575; 53 72: 0.55; 53 73: 0.475; 53 74: 0.44; 53 75: 0.38
153 | 46 | 53 43: 72.5; 53 44: 60; 53 45: 48; 53 46: 44; 53 47: 38; 53 48: 33; 53 49: 31; 53 50: 22; 53 51: 15; 53 52: 15; 53 53: 11.5; 53 54: 9; 53 55: 7; 53 56: 6.25; 53 57: 5; 53 58: 4.25; 53 59: 3.5; 53 60: 3.2; 53 61: 2.6; 53 62: 2.3; 53 63: 1.95; 53 64: 1.7; 53 65: 1.35; 53 66: 1.3; 53 67: 1.15; 53 68: 1; 53 69: 0.85; 53 70: 0.775; 53 71: 0.625; 53 72: 0.6; 53 73: 0.525; 53 74: 0.475; 53 75: 0.425
154 | 48 | 53 43: 80; 53 44: 65; 53 45: 52.5; 53 46: 48; 53 47: 42.5; 53 48: 36; 53 49: 34; 53 50: 24; 53 51: 17; 53 52: 16; 53 53: 12.5; 53 54: 10; 53 55: 7.5; 53 56: 6.75; 53 57: 5.5; 53 58: 4.75; 53 59: 3.8; 53 60: 3.4; 53 61: 2.8; 53 62: 2.4; 53 63: 2.1; 53 64: 1.85; 53 65: 1.5; 53 66: 1.4; 53 67: 1.25; 53 68: 1.075; 53 69: 0.925; 53 70: 0.85; 53 71: 0.675; 53 72: 0.65; 53 73: 0.575; 53 74: 0.525; 53 75: 0.45
155 | 50 | 53 44: 70; 53 45: 57.5; 53 46: 50; 53 47: 45; 53 48: 39; 53 49: 36; 53 50: 26; 53 51: 18; 53 52: 17; 53 53: 13.5; 53 54: 10.5; 53 55: 8; 53 56: 7.25; 53 57: 6; 53 58: 5; 53 59: 4; 53 60: 3.7; 53 61: 3; 53 62: 2.6; 53 63: 2.3; 53 64: 2; 53 65: 1.6; 53 66: 1.5; 53 67: 1.35; 53 68: 1.15; 53 69: 1; 53 70: 0.9; 53 71: 0.725; 53 72: 0.7; 53 73: 0.625; 53 74: 0.55; 53 75: 0.475

## x
Richtlijnen voor aan te houden luchtsnelheden
Bedrijf/persoon | Vanaf LBK naar hoofdkanaal | Aftakking van hoofdkanaal | horizontale distributiekanalen | aftakkingen naar roosters | bij/aansluiting op roosters
Peter de Jong (Burgers Ergon) | 8 - 6 | 5 | 5 - 3,5 | 3,5 - 3 | 3 - 2,5
Remy Krom (Uticon Dynatherm) | 5 |  | 4,5 - 4 |  | 3 - 2,5
Schreuder Groep (uit een bestek) | 6 | 6 | 4* - 3** |  | 2,5
*: in gangen, **: in verblijfsgebieden (ook voor verticale kanalen?)
Maximaal luchtdebiet [m3/h] om gegeven luchtsnelheid niet te overschrijden
|  | nom D. | Luchtsnelheid [m/s]
|  | [mm] | 2.5 | 3 | 3.5 | 4 | 4.5 | 5 | 6 | 7 | 8
|  | 80 | 45.2389 | 66.6884 | 77.8032 | 88.9179 | 100.0326 | 111.1474 | 133.3769 | 155.6063 | 177.8358
|  | 90 | 57.2555 | 103.471 | 120.7161 | 137.9613 | 155.2064 | 172.4516 | 206.9419 | 241.4322 | 275.9226
|  | 100 | 70.6858 | 85 | 99 | 113 | 127 | 141 | 170 | 198 | 226
|  | 112 | 88.6683 | 277.7527 | 324.0449 | 370.337 | 416.6291 | 462.9212 | 555.5055 | 648.0897 | 740.674
|  | 125 | 110.4466 | 133 | 155 | 177 | 199 | 221 | 265 | 309 | 353
|  | 150 | 159.0431 | 178.7978 | 225.9731 | 360.9491 | 920.9253 | 5994.8897 | 254035.7225 | 456165014.0602 | 1.4709e+15
|  | 160 | 180.9557 | 217 | 253 | 290 | 326 | 362 | 434 | 507 | 579
|  | 180 | 229.0221 | 1655.5353 | 1931.4579 | 2207.3804 | 2483.303 | 2759.2255 | 3311.0707 | 3862.9158 | 4414.7609
|  | 200 | 282.7433 | 339 | 396 | 452 | 509 | 565 | 679 | 792 | 905
|  | 225 | 357.847 | 4172.7334 | 4868.1889 | 5563.6445 | 6259.1 | 6954.5556 | 8345.4667 | 9736.3778 | 11127.289
|  | 250 | 441.7865 | 530 | 619 | 707 | 795 | 884 | 1060 | 1237 | 1414
|  | 280 | 554.1769 | 26488.5653 | 30903.3262 | 35318.087 | 39732.8479 | 44147.6088 | 52977.1305 | 61806.6523 | 70636.1741
|  | 315 | 701.3802 | 842 | 982 | 1122 | 1262 | 1403 | 1683 | 1964 | 2244
|  | 400 | 1130.9734 | 1357 | 1583 | 1810 | 2036 | 2262 | 2714 | 3167 | 3619
|  | 500 | 1767.1459 | 2121 | 2474 | 2827 | 3181 | 3534 | 4241 | 4948 | 5655